## Transmission lines
| Investment cost |  | 3.2965 | EUR/MW/m
|  |  | 3.2965 | MEUR/GW/KM |  |  |  | Distance (km) | INVCOST (MEUR/GW) | FIXEDCOST 2030 (MEUR/GW/year) | FIXEDCOST 2050 (MEUR/GW/year)
[8 empty] | 10 | 423.9946 | 0.27472 | 0.28804
[8 empty] | 20 | 439.1421 | 0.54944 | 0.57608
|  |  | 2020 | 2030 | 2050 |  |  | 30 | 454.2895 | 0.82416 | 0.86412
| Fixed OM |  | 26.2015 | 27.4719 | 28.8039 | EUR/MW/KM/year |  | 40 | 469.437 | 1.0989 | 1.1522
|  |  | 0.026201 | 0.027472 | 0.028804 | MEUR/GW/KM/year |  | 50 | 484.5845 | 1.3736 | 1.4402
[8 empty] | 60 | 499.7319 | 1.6483 | 1.7282
[8 empty] | 70 | 514.8794 | 1.923 | 2.0163
| Energy losses (efficiency) |  |  | 0.3% |  |  |  | 80 | 530.0268 | 2.1977 | 2.3043
[8 empty] | 90 | 545.1743 | 2.4725 | 2.5923
| Technical life time [years] | 40 | [5 empty] | 100 | 560.3217 | 2.7472 | 2.8804
| Typical load profile (-) | 45% | [5 empty] | 110 | 575.4692 | 3.0219 | 3.1684
| Construction time [years] | 1.5 | [5 empty] | 120 | 590.6166 | 3.2966 | 3.4565
[8 empty] | 130 | 605.7641 | 3.5713 | 3.7445
| Reinforcement costs [EUR/MW] | 16801 | 16.801 | MEUR/GW |  |  |  | 140 | 620.9115 | 3.8461 | 4.0325
| Investment costs; type 1 station [EUR/MW] | 80816.3266 | 80.8163 | MEUR/GW |  |  |  | 150 | 636.059 | 4.1208 | 4.3206
| Investment costs; type 2 station [EUR/MW] | 4759.6563 | 4.7597 | MEUR/GW |  |  |  | 160 | 651.2064 | 4.3955 | 4.6086
[8 empty] | 170 | 666.3539 | 4.6702 | 4.8967
[8 empty] | 180 | 681.5013 | 4.9449 | 5.1847
[8 empty] | 190 | 696.6488 | 5.2197 | 5.4727
| baggrundsrapport_for_forudsaetninger_og_anvendte_data_i_cost_benefit_analyse_fra_2020.pdf | [6 empty] | 200 | 711.7962 | 5.4944 | 5.7608
[8 empty] | 210 | 726.9437 | 5.7691 | 6.0488
hvdc sea | 11.3 | mill kr/km |  | 7.46 | DKK/EUR |  |  | 220 | 742.0912 | 6.0438 | 6.3368
hvdc land | 10.8 | mill kr/km |  |  |  | 1GW CABLE |  | 230 | 757.2386 | 6.3185 | 6.6249
hvdc sea | 1.5147 | mill eur/km | [5 empty] | 240 | 772.3861 | 6.5932 | 6.9129
hvdc land | 1.4477 | mill eur/km | [5 empty] | 250 | 787.5335 | 6.868 | 7.201
| 1 gw aprox | [6 empty] | 260 | 802.681 | 7.1427 | 7.489
[8 empty] | 270 | 817.8284 | 7.4174 | 7.777
[8 empty] | 280 | 832.9759 | 7.6921 | 8.0651
[8 empty] | 290 | 848.1233 | 7.9668 | 8.3531
[8 empty] | 300 | 863.2708 | 8.2416 | 8.6412
| COSTS OF CABLES ARE NOT PER GW ACCORDING TO | cost_benefit_analyse_endelig_version.pdf | [5 empty] | 310 | 878.4182 | 8.5163 | 8.9292
[8 empty] | 320 | 893.5657 | 8.791 | 9.2172
[8 empty] | 330 | 908.7131 | 9.0657 | 9.5053
| DENMARK CONNECTION |  | 706.4343 | meur/gw |  |  |  | 340 | 923.8606 | 9.3404 | 9.7933
[8 empty] | 350 | 939.008 | 9.6152 | 10.0813
| Not platforms!!!! | [6 empty] | 360 | 954.1555 | 9.8899 | 10.3694
[8 empty] | 370 | 969.3029 | 10.1646 | 10.6574
[8 empty] | 380 | 984.4504 | 10.4393 | 10.9455
[8 empty] | 390 | 999.5979 | 10.714 | 11.2335
[8 empty] | 400 | 1014.7453 | 10.9887 | 11.5215
[8 empty] | 410 | 1029.8928 | 11.2635 | 11.8096
[8 empty] | 420 | 1045.0402 | 11.5382 | 12.0976
[8 empty] | 430 | 1060.1877 | 11.8129 | 12.3857
[8 empty] | 440 | 1075.3351 | 12.0876 | 12.6737
[8 empty] | 450 | 1090.4826 | 12.3623 | 12.9617
[8 empty] | 460 | 1105.63 | 12.6371 | 13.2498
[8 empty] | 470 | 1120.7775 | 12.9118 | 13.5378
[8 empty] | 480 | 1135.9249 | 13.1865 | 13.8258
[8 empty] | 490 | 1151.0724 | 13.4612 | 14.1139
[6 empty] | AC/DC in the island |  | 500 | 1166.2198 | 13.7359 | 14.4019
[8 empty] | 510 | 1181.3673 | 14.0107 | 14.69
[6 empty] | 1830 | milldkk | 520 | 1196.5147 | 14.2854 | 14.978
[8 empty] | 530 | 1211.6622 | 14.5601 | 15.266
[6 empty] | 245.3083 | millEUR | 540 | 1226.8097 | 14.8348 | 15.5541
[8 empty] | 550 | 1241.9571 | 15.1095 | 15.8421
[8 empty] | 560 | 1257.1046 | 15.3842 | 16.1302
[6 empty] | AC/DC in land |  | 570 | 1272.252 | 15.659 | 16.4182
[6 empty] | 1220 | milldkk | 580 | 1287.3995 | 15.9337 | 16.7062
[8 empty] | 590 | 1302.5469 | 16.2084 | 16.9943
[6 empty] | 163.5389 | millEUR | 600 | 1317.6944 | 16.4831 | 17.2823
[8 empty] | 610 | 1332.8418 | 16.7578 | 17.5704
[8 empty] | 620 | 1347.9893 | 17.0326 | 17.8584
[8 empty] | 630 | 1363.1367 | 17.3073 | 18.1464
[8 empty] | 640 | 1378.2842 | 17.582 | 18.4345
[8 empty] | 650 | 1393.4316 | 17.8567 | 18.7225
[8 empty] | 660 | 1408.5791 | 18.1314 | 19.0105
[8 empty] | 670 | 1423.7265 | 18.4062 | 19.2986
[8 empty] | 680 | 1438.874 | 18.6809 | 19.5866
[8 empty] | 690 | 1454.0214 | 18.9556 | 19.8747
[8 empty] | 700 | 1469.1689 | 19.2303 | 20.1627
[8 empty] | 710 | 1484.3164 | 19.505 | 20.4507
[8 empty] | 720 | 1499.4638 | 19.7797 | 20.7388
[8 empty] | 730 | 1514.6113 | 20.0545 | 21.0268
[8 empty] | 740 | 1529.7587 | 20.3292 | 21.3149
[8 empty] | 750 | 1544.9062 | 20.6039 | 21.6029
[8 empty] | 760 | 1560.0536 | 20.8786 | 21.8909
[8 empty] | 770 | 1575.2011 | 21.1533 | 22.179
[8 empty] | 780 | 1590.3485 | 21.4281 | 22.467
[8 empty] | 790 | 1605.496 | 21.7028 | 22.755
[8 empty] | 800 | 1620.6434 | 21.9775 | 23.0431
[8 empty] | 810 | 1635.7909 | 22.2522 | 23.3311
[8 empty] | 820 | 1650.9383 | 22.5269 | 23.6192
[8 empty] | 830 | 1666.0858 | 22.8016 | 23.9072
[8 empty] | 840 | 1681.2332 | 23.0764 | 24.1952
[8 empty] | 850 | 1696.3807 | 23.3511 | 24.4833
[8 empty] | 860 | 1711.5282 | 23.6258 | 24.7713
[8 empty] | 870 | 1726.6756 | 23.9005 | 25.0594
[8 empty] | 880 | 1741.8231 | 24.1752 | 25.3474
[8 empty] | 890 | 1756.9705 | 24.45 | 25.6354
[8 empty] | 900 | 1772.118 | 24.7247 | 25.9235
[8 empty] | 910 | 1787.2654 | 24.9994 | 26.2115
[8 empty] | 920 | 1802.4129 | 25.2741 | 26.4995
[8 empty] | 930 | 1817.5603 | 25.5488 | 26.7876
[8 empty] | 940 | 1832.7078 | 25.8236 | 27.0756
[8 empty] | 950 | 1847.8552 | 26.0983 | 27.3637
[8 empty] | 960 | 1863.0027 | 26.373 | 27.6517
[8 empty] | 970 | 1878.1501 | 26.6477 | 27.9397
[8 empty] | 980 | 1893.2976 | 26.9224 | 28.2278
[8 empty] | 990 | 1908.445 | 27.1971 | 28.5158
[8 empty] | 1000 | 1923.5925 | 27.4719 | 28.8039

## ELC_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/PJ out | PJ/PJ out | Factor | years | PJ/GW | M€ /GW | M€ /GW | M€ /PJ | years
TRANS_LINE | Transmission line |  | ELC | EXP_ELC |  | 2020 | 2030 | 0.997 |  |  | 0.45 | 40 | 31.536 | 706.4343 | 2.6201 |  | 1.5 | ~FI_Process
[6 empty] | 2030 |  | 0.997 |  |  | 0.45 | 40 | 31.536 | 706.4343 | 5.4944 |  | 1.5 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
[6 empty] | 2050 |  | 0.997 |  |  | 0.45 | 40 | 31.536 | 706.4343 | 5.7608 |  | 1.5 | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
*
[18 empty] | PRE | TRANS_LINE | Transmission line | PJ | GW | DAYNITE | EXP_ELC | YES
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## H2
PIPES |  |  |  |  | SHIPS
[5 empty] | no km?? |  |  |  | H2
Investment costs; single line, 1000-4000 MW [EUR/MW/m] | 0.42535 | 0.42535 | MEUR/GW/KM | [5 empty] | 33.33 | kwh/kg
Investment costs; single line, above 6000 MW [EUR/MW/m] | 0.24458 | 0.24458 | MEUR/GW/KM | [5 empty] | 33.33 | MWh/t
[9 empty] | 33.33 | mw/t | 0.03333 | GW/T
[9 empty] | 0.03333 | MWh/kg
Technical life time [years] | 50 |  |  |  | Technical life time [years] | 20
Construction time [years] | 1
| 2030 | 2050 | [6 empty] | MWh-->pj
Fixed O&M [EUR/km/year/MW] | 0.26584 | 0.19938 | [6 empty] | 3.6e-06 |  |  |  | Typical ship
MEUR/KM/YEAR/GW | 0.00026584 | 0.00019938 |  |  |  | 2030 | 2050 | [5 empty] | 10000 | tons
[5 empty] | LH2: Energy demand [MJ/km] | 2025 | 1575
[5 empty] | PJ/KM | 0.002025 | 0.001575 | [5 empty] | 1.1999 | PJ
| 2030 | 2050 |  |  | LH2 Investment cost [EUR/tonH2] | 14887.2181 | 10633.7272
Energy losses, lines 1500-5000 MW, [%/1000 km] | 2.5 | 2.2 |  |  | LH2: Fixed O&M cost [EUR/tonH2/y] | 74.4361 | 53.1686
Energy losses, lines 5000-20000 MW, [%/1000 km] | 1.9 | 1.7 |  |  | LH2: Port cost [EUR/tonH2] | 6.3802 | 4.2535
Energy demand, compressor filling station [% | 1.68 | 1.47
[5 empty] | LH2 Investment cost [MEUR/PJ] | 124.0726 | 88.6233
Distance (km) | INVCOST (MEUR/GW) 1000-4000 | INVCOST (MEUR/GW) 6000 | FIXEDCOST 2030 (MEUR/GW/year) | FIXEDCOST 2050 (MEUR/GW/year) | LH2: Fixed O&M cost [MEUR/PJ/y] | 0.62036 | 0.44312
10 | 4.2535 | 2.4458 | 0.0026584 | 0.0019938 | LH2: Port cost [MEUR/PJ] | 0.053174 | 0.035449
20 | 8.507 | 4.8915 | 0.0053169 | 0.0039876
30 | 12.7605 | 7.3373 | 0.0079753 | 0.0059815
40 | 17.014 | 9.783 | 0.010634 | 0.0079753 | Distance (km) |  |  | EFFICIENCY 2030 | EFFICIENCY 2050
50 | 21.2675 | 12.2288 | 0.013292 | 0.0099691 | 10 | 0.02025 | 0.01575 | 0.98312 | 0.98687
60 | 25.5209 | 14.6745 | 0.015951 | 0.011963 | 20 | 0.0405 | 0.0315 | 0.96625 | 0.97375
70 | 29.7744 | 17.1203 | 0.018609 | 0.013957 | 30 | 0.06075 | 0.04725 | 0.94937 | 0.96062
80 | 34.0279 | 19.5661 | 0.021267 | 0.015951 | 40 | 0.081 | 0.063 | 0.93249 | 0.94749
90 | 38.2814 | 22.0118 | 0.023926 | 0.017944 | 50 | 0.10125 | 0.07875 | 0.91562 | 0.93437
100 | 42.5349 | 24.4576 | 0.026584 | 0.019938 | 60 | 0.1215 | 0.0945 | 0.89874 | 0.92124
110 | 46.7884 | 26.9033 | 0.029243 | 0.021932 | 70 | 0.14175 | 0.11025 | 0.88186 | 0.90812
120 | 51.0419 | 29.3491 | 0.031901 | 0.023926 | 80 | 0.162 | 0.126 | 0.86499 | 0.89499
130 | 55.2954 | 31.7948 | 0.03456 | 0.02592 | 90 | 0.18225 | 0.14175 | 0.84811 | 0.88186
140 | 59.5489 | 34.2406 | 0.037218 | 0.027914 | 100 | 0.2025 | 0.1575 | 0.83123 | 0.86874
150 | 63.8024 | 36.6864 | 0.039876 | 0.029907 | 110 | 0.22275 | 0.17325 | 0.81436 | 0.85561
160 | 68.0559 | 39.1321 | 0.042535 | 0.031901 | 120 | 0.243 | 0.189 | 0.79748 | 0.84248
170 | 72.3093 | 41.5779 | 0.045193 | 0.033895 | 130 | 0.26325 | 0.20475 | 0.7806 | 0.82936
180 | 76.5628 | 44.0236 | 0.047852 | 0.035889 | 140 | 0.2835 | 0.2205 | 0.76373 | 0.81623
190 | 80.8163 | 46.4694 | 0.05051 | 0.037883 | 150 | 0.30375 | 0.23625 | 0.74685 | 0.80311
200 | 85.0698 | 48.9151 | 0.053169 | 0.039876 | 160 | 0.324 | 0.252 | 0.72997 | 0.78998
210 | 89.3233 | 51.3609 | 0.055827 | 0.04187 | 170 | 0.34425 | 0.26775 | 0.7131 | 0.77685
220 | 93.5768 | 53.8067 | 0.058485 | 0.043864 | 180 | 0.3645 | 0.2835 | 0.69622 | 0.76373
230 | 97.8303 | 56.2524 | 0.061144 | 0.045858 | 190 | 0.38475 | 0.29925 | 0.67934 | 0.7506
240 | 102.0838 | 58.6982 | 0.063802 | 0.047852 | 200 | 0.405 | 0.315 | 0.66247 | 0.73747
250 | 106.3373 | 61.1439 | 0.066461 | 0.049846 | 210 | 0.42525 | 0.33075 | 0.64559 | 0.72435
260 | 110.5908 | 63.5897 | 0.069119 | 0.051839 | 220 | 0.4455 | 0.3465 | 0.62871 | 0.71122
270 | 114.8443 | 66.0354 | 0.071778 | 0.053833 | 230 | 0.46575 | 0.36225 | 0.61184 | 0.69809
280 | 119.0977 | 68.4812 | 0.074436 | 0.055827 | 240 | 0.486 | 0.378 | 0.59496 | 0.68497
290 | 123.3512 | 70.927 | 0.077095 | 0.057821 | 250 | 0.50625 | 0.39375 | 0.57808 | 0.67184
300 | 127.6047 | 73.3727 | 0.079753 | 0.059815 | 260 | 0.5265 | 0.4095 | 0.56121 | 0.65872
310 | 131.8582 | 75.8185 | 0.082411 | 0.061809 | 270 | 0.54675 | 0.42525 | 0.54433 | 0.64559
320 | 136.1117 | 78.2642 | 0.08507 | 0.063802 | 280 | 0.567 | 0.441 | 0.52745 | 0.63246
330 | 140.3652 | 80.71 | 0.087728 | 0.065796 | 290 | 0.58725 | 0.45675 | 0.51058 | 0.61934
340 | 144.6187 | 83.1557 | 0.090387 | 0.06779 | 300 | 0.6075 | 0.4725 | 0.4937 | 0.60621
350 | 148.8722 | 85.6015 | 0.093045 | 0.069784 | 310 | 0.62775 | 0.48825 | 0.47682 | 0.59308
360 | 153.1257 | 88.0473 | 0.095704 | 0.071778 | 320 | 0.648 | 0.504 | 0.45995 | 0.57996
370 | 157.3792 | 90.493 | 0.098362 | 0.073771 | 330 | 0.66825 | 0.51975 | 0.44307 | 0.56683
380 | 161.6327 | 92.9388 | 0.10102 | 0.075765 | 340 | 0.6885 | 0.5355 | 0.42619 | 0.55371
390 | 165.8861 | 95.3845 | 0.10368 | 0.077759 | 350 | 0.70875 | 0.55125 | 0.40932 | 0.54058
400 | 170.1396 | 97.8303 | 0.10634 | 0.079753 | 360 | 0.729 | 0.567 | 0.39244 | 0.52745
410 | 174.3931 | 100.276 | 0.109 | 0.081747 | 370 | 0.74925 | 0.58275 | 0.37556 | 0.51433
420 | 178.6466 | 102.7218 | 0.11165 | 0.083741 | 380 | 0.7695 | 0.5985 | 0.35869 | 0.5012
430 | 182.9001 | 105.1676 | 0.11431 | 0.085734 | 390 | 0.78975 | 0.61425 | 0.34181 | 0.48807
440 | 187.1536 | 107.6133 | 0.11697 | 0.087728 | 400 | 0.81 | 0.63 | 0.32493 | 0.47495
450 | 191.4071 | 110.0591 | 0.11963 | 0.089722 | 410 | 0.83025 | 0.64575 | 0.30806 | 0.46182
460 | 195.6606 | 112.5048 | 0.12229 | 0.091716 | 420 | 0.8505 | 0.6615 | 0.29118 | 0.44869
470 | 199.9141 | 114.9506 | 0.12495 | 0.09371 | 430 | 0.87075 | 0.67725 | 0.2743 | 0.43557
480 | 204.1676 | 117.3963 | 0.1276 | 0.095704 | 440 | 0.891 | 0.693 | 0.25743 | 0.42244
490 | 208.4211 | 119.8421 | 0.13026 | 0.097697 | 450 | 0.91125 | 0.70875 | 0.24055 | 0.40932
500 | 212.6745 | 122.2879 | 0.13292 | 0.099691 | 460 | 0.9315 | 0.7245 | 0.22367 | 0.39619
510 | 216.928 | 124.7336 | 0.13558 | 0.10169 | 470 | 0.95175 | 0.74025 | 0.2068 | 0.38306
520 | 221.1815 | 127.1794 | 0.13824 | 0.10368 | 480 | 0.972 | 0.756 | 0.18992 | 0.36994
530 | 225.435 | 129.6251 | 0.1409 | 0.10567 | 490 | 0.99225 | 0.77175 | 0.17304 | 0.35681
540 | 229.6885 | 132.0709 | 0.14356 | 0.10767 | 500 | 1.0125 | 0.7875 | 0.15617 | 0.34368
550 | 233.942 | 134.5166 | 0.14621 | 0.10966 | 510 | 1.0327 | 0.80325 | 0.13929 | 0.33056
560 | 238.1955 | 136.9624 | 0.14887 | 0.11165 | 520 | 1.053 | 0.819 | 0.12241 | 0.31743
570 | 242.449 | 139.4082 | 0.15153 | 0.11365 | 530 | 1.0733 | 0.83475 | 0.10554 | 0.30431
580 | 246.7025 | 141.8539 | 0.15419 | 0.11564 | 540 | 1.0935 | 0.8505 | 0.088659 | 0.29118
590 | 250.956 | 144.2997 | 0.15685 | 0.11764 | 550 | 1.1138 | 0.86625 | 0.071782 | 0.27805
600 | 255.2095 | 146.7454 | 0.15951 | 0.11963 | 560 | 1.134 | 0.882 | 0.054905 | 0.26493
610 | 259.4629 | 149.1912 | 0.16216 | 0.12162 | 570 | 1.1542 | 0.89775 | 0.038029 | 0.2518
620 | 263.7164 | 151.6369 | 0.16482 | 0.12362 | 580 | 1.1745 | 0.9135 | 0.021152 | 0.23867
630 | 267.9699 | 154.0827 | 0.16748 | 0.12561 | 590 | 1.1947 | 0.92925 | 0.0042754 | 0.22555
640 | 272.2234 | 156.5285 | 0.17014 | 0.1276 | 600 | 1.215 | 0.945 | -0.012601 | 0.21242
650 | 276.4769 | 158.9742 | 0.1728 | 0.1296 | 610 | 1.2352 | 0.96075 | -0.029478 | 0.19929
660 | 280.7304 | 161.42 | 0.17546 | 0.13159 | 620 | 1.2555 | 0.9765 | -0.046355 | 0.18617
670 | 284.9839 | 163.8657 | 0.17811 | 0.13359 | 630 | 1.2757 | 0.99225 | -0.063231 | 0.17304
680 | 289.2374 | 166.3115 | 0.18077 | 0.13558 | 640 | 1.296 | 1.008 | -0.080108 | 0.15992
690 | 293.4909 | 168.7573 | 0.18343 | 0.13757 | 650 | 1.3162 | 1.0237 | -0.096985 | 0.14679
700 | 297.7444 | 171.203 | 0.18609 | 0.13957 | 660 | 1.3365 | 1.0395 | -0.11386 | 0.13366
710 | 301.9979 | 173.6488 | 0.18875 | 0.14156 | 670 | 1.3567 | 1.0553 | -0.13074 | 0.12054
720 | 306.2513 | 176.0945 | 0.19141 | 0.14356 | 680 | 1.377 | 1.071 | -0.14761 | 0.10741
730 | 310.5048 | 178.5403 | 0.19407 | 0.14555 | 690 | 1.3972 | 1.0868 | -0.16449 | 0.094284
740 | 314.7583 | 180.986 | 0.19672 | 0.14754 | 700 | 1.4175 | 1.1025 | -0.18137 | 0.081158
750 | 319.0118 | 183.4318 | 0.19938 | 0.14954 | 710 | 1.4377 | 1.1182 | -0.19824 | 0.068032
760 | 323.2653 | 185.8776 | 0.20204 | 0.15153 | 720 | 1.458 | 1.134 | -0.21512 | 0.054905
770 | 327.5188 | 188.3233 | 0.2047 | 0.15352 | 730 | 1.4782 | 1.1498 | -0.232 | 0.041779
780 | 331.7723 | 190.7691 | 0.20736 | 0.15552 | 740 | 1.4985 | 1.1655 | -0.24887 | 0.028653
790 | 336.0258 | 193.2148 | 0.21002 | 0.15751 | 750 | 1.5187 | 1.1812 | -0.26575 | 0.015527
800 | 340.2793 | 195.6606 | 0.21267 | 0.15951 | 760 | 1.539 | 1.197 | -0.28263 | 0.0024002
810 | 344.5328 | 198.1063 | 0.21533 | 0.1615 | 770 | 1.5593 | 1.2127 | -0.2995 | -0.010726
820 | 348.7863 | 200.5521 | 0.21799 | 0.16349 | 780 | 1.5795 | 1.2285 | -0.31638 | -0.023852
830 | 353.0397 | 202.9979 | 0.22065 | 0.16549 | 790 | 1.5998 | 1.2443 | -0.33326 | -0.036979
840 | 357.2932 | 205.4436 | 0.22331 | 0.16748 | 800 | 1.62 | 1.26 | -0.35014 | -0.050105
850 | 361.5467 | 207.8894 | 0.22597 | 0.16948 | 810 | 1.6402 | 1.2757 | -0.36701 | -0.063231
860 | 365.8002 | 210.3351 | 0.22863 | 0.17147 | 820 | 1.6605 | 1.2915 | -0.38389 | -0.076358
870 | 370.0537 | 212.7809 | 0.23128 | 0.17346 | 830 | 1.6807 | 1.3073 | -0.40077 | -0.089484
880 | 374.3072 | 215.2266 | 0.23394 | 0.17546 | 840 | 1.701 | 1.323 | -0.41764 | -0.10261
890 | 378.5607 | 217.6724 | 0.2366 | 0.17745 | 850 | 1.7212 | 1.3388 | -0.43452 | -0.11574
900 | 382.8142 | 220.1182 | 0.23926 | 0.17944 | 860 | 1.7415 | 1.3545 | -0.4514 | -0.12886
910 | 387.0677 | 222.5639 | 0.24192 | 0.18144 | 870 | 1.7617 | 1.3702 | -0.46827 | -0.14199
920 | 391.3212 | 225.0097 | 0.24458 | 0.18343 | 880 | 1.782 | 1.386 | -0.48515 | -0.15512
930 | 395.5747 | 227.4554 | 0.24723 | 0.18543 | 890 | 1.8022 | 1.4018 | -0.50203 | -0.16824
940 | 399.8281 | 229.9012 | 0.24989 | 0.18742 | 900 | 1.8225 | 1.4175 | -0.5189 | -0.18137
950 | 404.0816 | 232.3469 | 0.25255 | 0.18941 | 910 | 1.8427 | 1.4332 | -0.53578 | -0.19449
960 | 408.3351 | 234.7927 | 0.25521 | 0.19141 | 920 | 1.863 | 1.449 | -0.55266 | -0.20762
970 | 412.5886 | 237.2385 | 0.25787 | 0.1934 | 930 | 1.8832 | 1.4647 | -0.56953 | -0.22075
980 | 416.8421 | 239.6842 | 0.26053 | 0.19539 | 940 | 1.9035 | 1.4805 | -0.58641 | -0.23387
990 | 421.0956 | 242.13 | 0.26318 | 0.19739 | 950 | 1.9237 | 1.4963 | -0.60329 | -0.247
1000 | 425.3491 | 244.5757 | 0.26584 | 0.19938 | 960 | 1.944 | 1.512 | -0.62016 | -0.26013
[5 empty] | 970 | 1.9642 | 1.5277 | -0.63704 | -0.27325
[5 empty] | 980 | 1.9845 | 1.5435 | -0.65392 | -0.28638
[5 empty] | 990 | 2.0048 | 1.5593 | -0.67079 | -0.2995
[5 empty] | 1000 | 2.025 | 1.575 | -0.68767 | -0.31263

## H2_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/PJ out | PJ/PJ out | Factor | years | PJ/GW | M€ /GW or M€/Pja | M€ /GW or M€/Pja | M€ /PJ | years
h2_pipe | Hydrogen Pipeline |  | H2 | EXP_H2 |  | 2020 | 2030 | 0.97 |  |  | 0.95 | 50 | 31.536 | 48.9151 | 0.053169 |  | 1 | ~FI_Process
[6 empty] | 2030 |  | 0.97 |  |  | 0.95 | 50 | 31.536 | 48.9151 | 0.053169 |  | 1 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
[6 empty] | 2050 |  | 0.97 |  |  | 0.95 | 50 | 31.536 | 48.9151 | 0.039876 |  | 1 | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
h2_ship | Hydrogen ship |  | H2 | EXP_H2 |  | 2020 | 2030 | 0.66247 |  |  | 0.95 | 20 | 1 | 1.3603 | 0.0067985 |  |  | *
[6 empty] | 2030 |  | 0.64559 |  |  | 0.95 | 20 | 1 | 1.3603 | 0.0067985 |  |  | PRE | h2_pipe | Hydrogen Pipeline | PJ | GW | DAYNITE | EXP_H2 | YES
[6 empty] | 2050 |  | 0.72435 |  |  | 0.95 | 20 | 1 | 0.9716 | 0.0048561 |  |  | PRE | h2_ship | Hydrogen ship | PJ | Pja | DAYNITE | EXP_H2 | YES
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## NH3
| PIPES |  |  | SHIPS |  |  |  |  | NH3=L20 in technology cathalogue SHIPS
no km??
[5 empty] | 2030 | 2050 |  |  | NH3
Energy losses [‰] | <0.1 |  |  | L20: Energy demand [MJ/km] | 2205 | 1715 |  |  | 5.2 | kwh/kg
Technical life time [years] | 50 |  |  | pj/km | 0.002205 | 0.001715 |  |  | 5.2 | MWh/t
Construction time [years] | 1 |  |  | L20: Investment cost [EUR/tonL20] | 1978.8327 | 1978.8327 |  |  | 5.2 | mw/t | 0.0052 | GW/T
|  |  |  | L20:Fixed O&M cost [EUR/tonL20/y] | 9.5704 | 9.5704 |  |  | 0.0052 | MWh/kg
| 2030 and 2050 |  |  | L20: Port cost [EUR/tonL20] | 1.8077 | 1.8077
Investment costs; single line, 1000-2000 MW [EUR/MW/m] | 0.21267 | 0.21267 | MEUR/GW/KM
Investment costs; single line, above 2000 MW [EUR/MW/m] | 0.21267 | 0.21267 | MEUR/GW/KM | L20: Investment cost [MEUR/PJ] | 105.7069 | 105.7069
|  |  |  | L20:Fixed O&M cost [MEUR/PJ/y] | 0.51124 | 0.51124 |  |  |  | MWh-->pj
Fixed O&M [EUR/km/year] | 106.3373 | 0.00010634 | MEUR/KM/YEAR | L20: Port cost [MEUR/PJ] | 0.096567 | 0.096567 |  |  |  | 3.6e-06
Typical ship
[13 empty] | 45000 | tons
Distance (km) | INVCOST (MEUR/GW) | FIXEDCOST 2030 (MEUR/year) |  | Technical life time [years] | 20
10 | 2.1267 | 0.0010634 | [10 empty] | 0.8424 | pj
20 | 4.2535 | 0.0021267
30 | 6.3802 | 0.0031901
40 | 8.507 | 0.0042535
50 | 10.6337 | 0.0053169
60 | 12.7605 | 0.0063802 |  | Distance (km) |  |  | EFFICIENCY 2030 | EFFICIENCY 2050
70 | 14.8872 | 0.0074436 |  | 10 | 0.02205 | 0.01715 | 0.97382 | 0.97964
80 | 17.014 | 0.008507 |  | 20 | 0.0441 | 0.0343 | 0.94765 | 0.95928
90 | 19.1407 | 0.0095704 |  | 30 | 0.06615 | 0.05145 | 0.92147 | 0.93892
100 | 21.2675 | 0.010634 |  | 40 | 0.0882 | 0.0686 | 0.8953 | 0.91857
110 | 23.3942 | 0.011697 |  | 50 | 0.11025 | 0.08575 | 0.86912 | 0.89821
120 | 25.5209 | 0.01276 |  | 60 | 0.1323 | 0.1029 | 0.84295 | 0.87785
130 | 27.6477 | 0.013824 |  | 70 | 0.15435 | 0.12005 | 0.81677 | 0.85749
140 | 29.7744 | 0.014887 |  | 80 | 0.1764 | 0.1372 | 0.7906 | 0.83713
150 | 31.9012 | 0.015951 |  | 90 | 0.19845 | 0.15435 | 0.76442 | 0.81677
160 | 34.0279 | 0.017014 |  | 100 | 0.2205 | 0.1715 | 0.73825 | 0.79642
170 | 36.1547 | 0.018077 |  | 110 | 0.24255 | 0.18865 | 0.71207 | 0.77606
180 | 38.2814 | 0.019141 |  | 120 | 0.2646 | 0.2058 | 0.6859 | 0.7557
190 | 40.4082 | 0.020204 |  | 130 | 0.28665 | 0.22295 | 0.65972 | 0.73534
200 | 42.5349 | 0.021267 |  | 140 | 0.3087 | 0.2401 | 0.63355 | 0.71498
210 | 44.6617 | 0.022331 |  | 150 | 0.33075 | 0.25725 | 0.60737 | 0.69462
220 | 46.7884 | 0.023394 |  | 160 | 0.3528 | 0.2744 | 0.5812 | 0.67426
230 | 48.9151 | 0.024458 |  | 170 | 0.37485 | 0.29155 | 0.55502 | 0.65391
240 | 51.0419 | 0.025521 |  | 180 | 0.3969 | 0.3087 | 0.52885 | 0.63355
250 | 53.1686 | 0.026584 |  | 190 | 0.41895 | 0.32585 | 0.50267 | 0.61319
260 | 55.2954 | 0.027648 |  | 200 | 0.441 | 0.343 | 0.4765 | 0.59283
270 | 57.4221 | 0.028711 |  | 210 | 0.46305 | 0.36015 | 0.45032 | 0.57247
280 | 59.5489 | 0.029774 |  | 220 | 0.4851 | 0.3773 | 0.42415 | 0.55211
290 | 61.6756 | 0.030838 |  | 230 | 0.50715 | 0.39445 | 0.39797 | 0.53175
300 | 63.8024 | 0.031901 |  | 240 | 0.5292 | 0.4116 | 0.37179 | 0.5114
310 | 65.9291 | 0.032965 |  | 250 | 0.55125 | 0.42875 | 0.34562 | 0.49104
320 | 68.0559 | 0.034028 |  | 260 | 0.5733 | 0.4459 | 0.31944 | 0.47068
330 | 70.1826 | 0.035091 |  | 270 | 0.59535 | 0.46305 | 0.29327 | 0.45032
340 | 72.3093 | 0.036155 |  | 280 | 0.6174 | 0.4802 | 0.26709 | 0.42996
350 | 74.4361 | 0.037218 |  | 290 | 0.63945 | 0.49735 | 0.24092 | 0.4096
360 | 76.5628 | 0.038281 |  | 300 | 0.6615 | 0.5145 | 0.21474 | 0.38925
370 | 78.6896 | 0.039345 |  | 310 | 0.68355 | 0.53165 | 0.18857 | 0.36889
380 | 80.8163 | 0.040408 |  | 320 | 0.7056 | 0.5488 | 0.16239 | 0.34853
390 | 82.9431 | 0.041472 |  | 330 | 0.72765 | 0.56595 | 0.13622 | 0.32817
400 | 85.0698 | 0.042535 |  | 340 | 0.7497 | 0.5831 | 0.11004 | 0.30781
410 | 87.1966 | 0.043598 |  | 350 | 0.77175 | 0.60025 | 0.083868 | 0.28745
420 | 89.3233 | 0.044662 |  | 360 | 0.7938 | 0.6174 | 0.057692 | 0.26709
430 | 91.4501 | 0.045725 |  | 370 | 0.81585 | 0.63455 | 0.031517 | 0.24674
440 | 93.5768 | 0.046788 |  | 380 | 0.8379 | 0.6517 | 0.0053419 | 0.22638
450 | 95.7035 | 0.047852 |  | 390 | 0.85995 | 0.66885 | -0.020833 | 0.20602
460 | 97.8303 | 0.048915 |  | 400 | 0.882 | 0.686 | -0.047009 | 0.18566
470 | 99.957 | 0.049979 |  | 410 | 0.90405 | 0.70315 | -0.073184 | 0.1653
480 | 102.0838 | 0.051042 |  | 420 | 0.9261 | 0.7203 | -0.099359 | 0.14494
490 | 104.2105 | 0.052105 |  | 430 | 0.94815 | 0.73745 | -0.12553 | 0.12458
500 | 106.3373 | 0.053169 |  | 440 | 0.9702 | 0.7546 | -0.15171 | 0.10423
510 | 108.464 | 0.054232 |  | 450 | 0.99225 | 0.77175 | -0.17788 | 0.083868
520 | 110.5908 | 0.055295 |  | 460 | 1.0143 | 0.7889 | -0.20406 | 0.063509
530 | 112.7175 | 0.056359 |  | 470 | 1.0363 | 0.80605 | -0.23024 | 0.043151
540 | 114.8443 | 0.057422 |  | 480 | 1.0584 | 0.8232 | -0.25641 | 0.022792
550 | 116.971 | 0.058485 |  | 490 | 1.0804 | 0.84035 | -0.28259 | 0.0024335
560 | 119.0977 | 0.059549 |  | 500 | 1.1025 | 0.8575 | -0.30876 | -0.017925
570 | 121.2245 | 0.060612 |  | 510 | 1.1245 | 0.87465 | -0.33494 | -0.038283
580 | 123.3512 | 0.061676 |  | 520 | 1.1466 | 0.8918 | -0.36111 | -0.058642
590 | 125.478 | 0.062739 |  | 530 | 1.1686 | 0.90895 | -0.38729 | -0.079
600 | 127.6047 | 0.063802 |  | 540 | 1.1907 | 0.9261 | -0.41346 | -0.099359
610 | 129.7315 | 0.064866 |  | 550 | 1.2127 | 0.94325 | -0.43964 | -0.11972
620 | 131.8582 | 0.065929 |  | 560 | 1.2348 | 0.9604 | -0.46581 | -0.14008
630 | 133.985 | 0.066992 |  | 570 | 1.2569 | 0.97755 | -0.49199 | -0.16043
640 | 136.1117 | 0.068056 |  | 580 | 1.2789 | 0.9947 | -0.51816 | -0.18079
650 | 138.2385 | 0.069119 |  | 590 | 1.301 | 1.0118 | -0.54434 | -0.20115
660 | 140.3652 | 0.070183 |  | 600 | 1.323 | 1.029 | -0.57051 | -0.22151
670 | 142.4919 | 0.071246 |  | 610 | 1.345 | 1.0461 | -0.59669 | -0.24187
680 | 144.6187 | 0.072309 |  | 620 | 1.3671 | 1.0633 | -0.62286 | -0.26223
690 | 146.7454 | 0.073373 |  | 630 | 1.3891 | 1.0804 | -0.64904 | -0.28259
700 | 148.8722 | 0.074436 |  | 640 | 1.4112 | 1.0976 | -0.67521 | -0.30294
710 | 150.9989 | 0.075499 |  | 650 | 1.4332 | 1.1147 | -0.70139 | -0.3233
720 | 153.1257 | 0.076563 |  | 660 | 1.4553 | 1.1319 | -0.72756 | -0.34366
730 | 155.2524 | 0.077626 |  | 670 | 1.4773 | 1.149 | -0.75374 | -0.36402
740 | 157.3792 | 0.07869 |  | 680 | 1.4994 | 1.1662 | -0.77991 | -0.38438
750 | 159.5059 | 0.079753 |  | 690 | 1.5214 | 1.1833 | -0.80609 | -0.40474
760 | 161.6327 | 0.080816 |  | 700 | 1.5435 | 1.2005 | -0.83226 | -0.42509
770 | 163.7594 | 0.08188 |  | 710 | 1.5655 | 1.2176 | -0.85844 | -0.44545
780 | 165.8861 | 0.082943 |  | 720 | 1.5876 | 1.2348 | -0.88462 | -0.46581
790 | 168.0129 | 0.084006 |  | 730 | 1.6097 | 1.2519 | -0.91079 | -0.48617
800 | 170.1396 | 0.08507 |  | 740 | 1.6317 | 1.2691 | -0.93697 | -0.50653
810 | 172.2664 | 0.086133 |  | 750 | 1.6538 | 1.2862 | -0.96314 | -0.52689
820 | 174.3931 | 0.087197 |  | 760 | 1.6758 | 1.3034 | -0.98932 | -0.54725
830 | 176.5199 | 0.08826 |  | 770 | 1.6978 | 1.3205 | -1.0155 | -0.5676
840 | 178.6466 | 0.089323 |  | 780 | 1.7199 | 1.3377 | -1.0417 | -0.58796
850 | 180.7734 | 0.090387 |  | 790 | 1.7419 | 1.3548 | -1.0678 | -0.60832
860 | 182.9001 | 0.09145 |  | 800 | 1.764 | 1.372 | -1.094 | -0.62868
870 | 185.0269 | 0.092513 |  | 810 | 1.786 | 1.3891 | -1.1202 | -0.64904
880 | 187.1536 | 0.093577 |  | 820 | 1.8081 | 1.4063 | -1.1464 | -0.6694
890 | 189.2803 | 0.09464 |  | 830 | 1.8301 | 1.4234 | -1.1725 | -0.68976
900 | 191.4071 | 0.095704 |  | 840 | 1.8522 | 1.4406 | -1.1987 | -0.71011
910 | 193.5338 | 0.096767 |  | 850 | 1.8742 | 1.4577 | -1.2249 | -0.73047
920 | 195.6606 | 0.09783 |  | 860 | 1.8963 | 1.4749 | -1.2511 | -0.75083
930 | 197.7873 | 0.098894 |  | 870 | 1.9183 | 1.492 | -1.2772 | -0.77119
940 | 199.9141 | 0.099957 |  | 880 | 1.9404 | 1.5092 | -1.3034 | -0.79155
950 | 202.0408 | 0.10102 |  | 890 | 1.9625 | 1.5263 | -1.3296 | -0.81191
960 | 204.1676 | 0.10208 |  | 900 | 1.9845 | 1.5435 | -1.3558 | -0.83226
970 | 206.2943 | 0.10315 |  | 910 | 2.0065 | 1.5606 | -1.3819 | -0.85262
980 | 208.4211 | 0.10421 |  | 920 | 2.0286 | 1.5778 | -1.4081 | -0.87298
990 | 210.5478 | 0.10527 |  | 930 | 2.0507 | 1.5949 | -1.4343 | -0.89334
1000 | 212.6745 | 0.10634 |  | 940 | 2.0727 | 1.6121 | -1.4605 | -0.9137
|  |  |  | 950 | 2.0947 | 1.6292 | -1.4866 | -0.93406
|  |  |  | 960 | 2.1168 | 1.6464 | -1.5128 | -0.95442
|  |  |  | 970 | 2.1389 | 1.6635 | -1.539 | -0.97477
|  |  |  | 980 | 2.1609 | 1.6807 | -1.5652 | -0.99513
|  |  |  | 990 | 2.1829 | 1.6978 | -1.5913 | -1.0155
|  |  |  | 1000 | 2.205 | 1.715 | -1.6175 | -1.0358

## NH3_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/PJ out | PJ/PJ out | Factor | years | PJ/GW | M€ /GW or M€/Pja | M€ /GW or M€/Pja | M€ /PJ | years
nh3_pipe | Ammonia Pipeline |  | AMM | EXP_AMM |  | 2020 | 2030 | 0.995 |  |  | 0.95 | 50 | 31.536 | 42.5349 | 0.021267 |  | 1 | ~FI_Process
[6 empty] | 2030 |  | 0.995 |  |  | 0.95 | 50 | 31.536 | 42.5349 | 0.021267 |  | 1 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
[6 empty] | 2050 |  | 0.995 |  |  | 0.95 | 50 | 31.536 | 42.5349 | 0.021267 |  | 1 | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
nh3_ship | Ammonia ship |  | AMM | EXP_AMM |  | 2020 | 2030 | 0.5 |  |  | 0.95 | 20 | 1 | 1.1595 | 0.0056026 |  |  | *
[6 empty] | 2030 |  | 0.5 |  |  | 0.95 | 20 | 1 | 1.1595 | 0.0056026 |  |  | PRE | nh3_pipe | Ammonia Pipeline | PJ | GW | DAYNITE | EXP_AMM | YES
[6 empty] | 2050 |  | 0.6 |  |  | 0.95 | 20 | 1 | 1.1595 | 0.0056026 |  |  | PRE | nh3_ship | Ammonia ship | PJ | Pja | DAYNITE | EXP_AMM | YES
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## CO2
|  | PIPES |  |  | DOES IT MAKE SENSE TO USE MW IN CO2?? |  | SHIPS
no km??
| Technical life time [years] | 50 |  |  |  | Technical life time CO₂ carrier [years] | 40
| Construction time [years] | 1 |  |  |  | Construction time [years] | 2
According to technology cathalogue, it is able to do 700 km per day
| Investment costs; offhore single line, 120 t CO₂/h [EUR/(tCO2/h)/m] | 33 | 3.7671e-06 | meur/kta/m |  |  | 2030 | 2050
[6 empty] | Energy demand, 4,000 t CO₂ ship (MWh/day) | 90 | 80 | 0.12857 | 0.11429 |  | MWh/km
| Fixed O&M [EUR/(tCO2/h)/year/km] | 20 | 2.2831e-06 | meur/kta/year/km |  | Energy demand, 10,000 t CO₂ ship (MWh/day) | 180 | 150 | 0.25714 | 0.21429
[6 empty] | Investments, 4000 t CO₂ ship (EUR/t CO₂) | 9082 | 7648
[6 empty] | Investments,10,000 t CO2 ship (EUR/t CO₂) | 5927.2 | 4780 | 100km | 12.8571 | 11.4286 |  | MWh
[6 empty] | Fixed O&M 4000 t CO₂ Ship (EUR/t CO₂/year) | 434.1196 | 365.5744 |  | 25.7143 | 21.4286
[6 empty] | Fixed O&M 10000 t CO₂ Ship (EUR/t CO₂/year) | 283.3202 | 228.484
[10 empty] | MWh-->pj |  | 4.6286e-05 | 4.1143e-05
Distance (km) | INVCOST (MEUR/kta) | FIXEDCOST (MEUR/kta/year) | [7 empty] | 3.6e-06 |  | 9.2571e-05 | 7.7143e-05
10 | 0.037671 | 2.2831e-05
20 | 0.075342 | 4.5662e-05
30 | 0.11301 | 6.8493e-05
40 | 0.15068 | 9.1324e-05
50 | 0.18836 | 0.00011416
60 | 0.22603 | 0.00013699
70 | 0.2637 | 0.00015982
80 | 0.30137 | 0.00018265
90 | 0.33904 | 0.00020548
100 | 0.37671 | 0.00022831
110 | 0.41438 | 0.00025114
120 | 0.45205 | 0.00027397
130 | 0.48973 | 0.0002968
140 | 0.5274 | 0.00031963
150 | 0.56507 | 0.00034247
160 | 0.60274 | 0.0003653
170 | 0.64041 | 0.00038813
180 | 0.67808 | 0.00041096
190 | 0.71575 | 0.00043379
200 | 0.75342 | 0.00045662
210 | 0.7911 | 0.00047945
220 | 0.82877 | 0.00050228
230 | 0.86644 | 0.00052511
240 | 0.90411 | 0.00054795
250 | 0.94178 | 0.00057078
260 | 0.97945 | 0.00059361
270 | 1.0171 | 0.00061644
280 | 1.0548 | 0.00063927
290 | 1.0925 | 0.0006621
300 | 1.1301 | 0.00068493
310 | 1.1678 | 0.00070776
320 | 1.2055 | 0.00073059
330 | 1.2432 | 0.00075342
340 | 1.2808 | 0.00077626
350 | 1.3185 | 0.00079909
360 | 1.3562 | 0.00082192
370 | 1.3938 | 0.00084475
380 | 1.4315 | 0.00086758
390 | 1.4692 | 0.00089041
400 | 1.5068 | 0.00091324
410 | 1.5445 | 0.00093607
420 | 1.5822 | 0.0009589
430 | 1.6199 | 0.00098174
440 | 1.6575 | 0.0010046
450 | 1.6952 | 0.0010274
460 | 1.7329 | 0.0010502
470 | 1.7705 | 0.0010731
480 | 1.8082 | 0.0010959
490 | 1.8459 | 0.0011187
500 | 1.8836 | 0.0011416
510 | 1.9212 | 0.0011644
520 | 1.9589 | 0.0011872
530 | 1.9966 | 0.00121
540 | 2.0342 | 0.0012329
550 | 2.0719 | 0.0012557
560 | 2.1096 | 0.0012785
570 | 2.1473 | 0.0013014
580 | 2.1849 | 0.0013242
590 | 2.2226 | 0.001347
600 | 2.2603 | 0.0013699
610 | 2.2979 | 0.0013927
620 | 2.3356 | 0.0014155
630 | 2.3733 | 0.0014384
640 | 2.411 | 0.0014612
650 | 2.4486 | 0.001484
660 | 2.4863 | 0.0015068
670 | 2.524 | 0.0015297
680 | 2.5616 | 0.0015525
690 | 2.5993 | 0.0015753
700 | 2.637 | 0.0015982
710 | 2.6747 | 0.001621
720 | 2.7123 | 0.0016438
730 | 2.75 | 0.0016667
740 | 2.7877 | 0.0016895
750 | 2.8253 | 0.0017123
760 | 2.863 | 0.0017352
770 | 2.9007 | 0.001758
780 | 2.9384 | 0.0017808
790 | 2.976 | 0.0018037
800 | 3.0137 | 0.0018265
810 | 3.0514 | 0.0018493
820 | 3.089 | 0.0018721
830 | 3.1267 | 0.001895
840 | 3.1644 | 0.0019178
850 | 3.2021 | 0.0019406
860 | 3.2397 | 0.0019635
870 | 3.2774 | 0.0019863
880 | 3.3151 | 0.0020091
890 | 3.3527 | 0.002032
900 | 3.3904 | 0.0020548
910 | 3.4281 | 0.0020776
920 | 3.4658 | 0.0021005
930 | 3.5034 | 0.0021233
940 | 3.5411 | 0.0021461
950 | 3.5788 | 0.0021689
960 | 3.6164 | 0.0021918
970 | 3.6541 | 0.0022146
980 | 3.6918 | 0.0022374
990 | 3.7295 | 0.0022603
1000 | 3.7671 | 0.0022831

## CO2_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/kt | PJ/PJ out | Factor | years | PJ/GW | M€ /kta | M€ /kta | M€ /PJ | years
co2_pipe | CO2 Pipeline |  | IMP_CO2 | CO2 |  | 2020 | 2030 | 0.995 |  |  | 0.95 | 50 | 1 | 0.75342 | 0.00045662 |  | 1 | ~FI_Process
[6 empty] | 2030 |  | 0.995 |  |  | 0.95 | 50 | 1 | 0.75342 | 0.00045662 |  | 1 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
[6 empty] | 2050 |  | 0.995 |  |  | 0.95 | 50 | 1 | 0.75342 | 0.00045662 |  | 1 | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
co2_ship | CO2 ship |  | IMP_CO2 | CO2 |  | 2020 | 2030 | 1 |  |  | 0.95 | 40 | 1 | 5.9272 | 0.28332 |  |  | *
|  | HFO |  |  |  | 2020 |  |  | 9.2571e-06 | [8 empty] | PRE | co2_pipe | CO2 Pipeline | kt | kta | DAYNITE | IMP_CO2 | YES
|  |  | IMP_CO2 | CO2 |  | 2030 |  | 1 |  |  | 0.95 | 40 | 1 | 5.9272 | 0.28332 |  |  | PRE | co2_ship | CO2 ship | kt | kta | DAYNITE | IMP_CO2 | YES
|  | HFO |  |  |  | 2030 |  |  | 9.2571e-06
|  |  | IMP_CO2 | CO2 |  | 2050 |  | 1 |  |  | 0.95 | 40 | 1 | 4.78 | 0.22848
|  | HFO |  |  |  | 2050 |  |  | 7.7143e-06
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## METHANOL
NO PIPES?? | SHIPS
| NO KM?? |  |  |  |  | Methanol=LHC in technology cathalogue
| Technical life time [years] | 20
Methanol
[6 empty] | 6.111 | kwh/kg
[6 empty] | 6.11 | MWh/t
|  | 2030 and 2050 | 2050 |  |  | 6.11 | mw/t | 0.00611 | GW/T
| LHC: Energy demand [MJ/km] | 2205 | 1715 |  |  | 0.00611 | MWh/kg
| pj/km | 0.002205 | 0.001715
| LHC: Investment cost [EUR/tonLHC] | 780.2255
| LHC: Fixed O&M cost [EUR/tonLHC/y] | 4.2535
| LHC: Port cost [EUR/tonLHC] | 1.4887 |  |  |  | MWh-->pj |  |  | Typical ship
[6 empty] | 3.6e-06 |  |  | 45000 | tons
| LHC: Investment cost [MEUR/PJ] | 35.4712 | [6 empty] | 0.98982 | PJ
| LHC: Fixed O&M cost [MEUR/PJ/y] | 0.19338
| LHC: Port cost [MEUR/PJ] | 0.067681
| Distance (km) |  |  | EFFICIENCY 2030 | EFFICIENCY 2050
| 10 | 0.02205 | 0.01715 | 0.97772 | 0.98267
| 20 | 0.0441 | 0.0343 | 0.95545 | 0.96535
| 30 | 0.06615 | 0.05145 | 0.93317 | 0.94802
| 40 | 0.0882 | 0.0686 | 0.91089 | 0.93069
| 50 | 0.11025 | 0.08575 | 0.88862 | 0.91337
| 60 | 0.1323 | 0.1029 | 0.86634 | 0.89604
| 70 | 0.15435 | 0.12005 | 0.84406 | 0.87872
| 80 | 0.1764 | 0.1372 | 0.82179 | 0.86139
| 90 | 0.19845 | 0.15435 | 0.79951 | 0.84406
| 100 | 0.2205 | 0.1715 | 0.77723 | 0.82674
| 110 | 0.24255 | 0.18865 | 0.75496 | 0.80941
| 120 | 0.2646 | 0.2058 | 0.73268 | 0.79208
| 130 | 0.28665 | 0.22295 | 0.7104 | 0.77476
| 140 | 0.3087 | 0.2401 | 0.68813 | 0.75743
| 150 | 0.33075 | 0.25725 | 0.66585 | 0.7401
| 160 | 0.3528 | 0.2744 | 0.64357 | 0.72278
| 170 | 0.37485 | 0.29155 | 0.62129 | 0.70545
| 180 | 0.3969 | 0.3087 | 0.59902 | 0.68813
| 190 | 0.41895 | 0.32585 | 0.57674 | 0.6708
| 200 | 0.441 | 0.343 | 0.55446 | 0.65347
| 210 | 0.46305 | 0.36015 | 0.53219 | 0.63615
| 220 | 0.4851 | 0.3773 | 0.50991 | 0.61882
| 230 | 0.50715 | 0.39445 | 0.48763 | 0.60149
| 240 | 0.5292 | 0.4116 | 0.46536 | 0.58417
| 250 | 0.55125 | 0.42875 | 0.44308 | 0.56684
| 260 | 0.5733 | 0.4459 | 0.4208 | 0.54951
| 270 | 0.59535 | 0.46305 | 0.39853 | 0.53219
| 280 | 0.6174 | 0.4802 | 0.37625 | 0.51486
| 290 | 0.63945 | 0.49735 | 0.35397 | 0.49753
| 300 | 0.6615 | 0.5145 | 0.3317 | 0.48021
| 310 | 0.68355 | 0.53165 | 0.30942 | 0.46288
| 320 | 0.7056 | 0.5488 | 0.28714 | 0.44556
| 330 | 0.72765 | 0.56595 | 0.26487 | 0.42823
| 340 | 0.7497 | 0.5831 | 0.24259 | 0.4109
| 350 | 0.77175 | 0.60025 | 0.22031 | 0.39358
| 360 | 0.7938 | 0.6174 | 0.19804 | 0.37625
| 370 | 0.81585 | 0.63455 | 0.17576 | 0.35892
| 380 | 0.8379 | 0.6517 | 0.15348 | 0.3416
| 390 | 0.85995 | 0.66885 | 0.13121 | 0.32427
| 400 | 0.882 | 0.686 | 0.10893 | 0.30694
| 410 | 0.90405 | 0.70315 | 0.086652 | 0.28962
| 420 | 0.9261 | 0.7203 | 0.064375 | 0.27229
| 430 | 0.94815 | 0.73745 | 0.042099 | 0.25497
| 440 | 0.9702 | 0.7546 | 0.019822 | 0.23764
| 450 | 0.99225 | 0.77175 | -0.002455 | 0.22031
| 460 | 1.0143 | 0.7889 | -0.024732 | 0.20299
| 470 | 1.0363 | 0.80605 | -0.047009 | 0.18566
| 480 | 1.0584 | 0.8232 | -0.069285 | 0.16833
| 490 | 1.0804 | 0.84035 | -0.091562 | 0.15101
| 500 | 1.1025 | 0.8575 | -0.11384 | 0.13368
| 510 | 1.1245 | 0.87465 | -0.13612 | 0.11635
| 520 | 1.1466 | 0.8918 | -0.15839 | 0.099028
| 530 | 1.1686 | 0.90895 | -0.18067 | 0.081702
| 540 | 1.1907 | 0.9261 | -0.20295 | 0.064375
| 550 | 1.2127 | 0.94325 | -0.22522 | 0.047049
| 560 | 1.2348 | 0.9604 | -0.2475 | 0.029723
| 570 | 1.2569 | 0.97755 | -0.26978 | 0.012396
| 580 | 1.2789 | 0.9947 | -0.29205 | -0.0049302
| 590 | 1.301 | 1.0118 | -0.31433 | -0.022257
| 600 | 1.323 | 1.029 | -0.33661 | -0.039583
| 610 | 1.345 | 1.0461 | -0.35888 | -0.056909
| 620 | 1.3671 | 1.0633 | -0.38116 | -0.074236
| 630 | 1.3891 | 1.0804 | -0.40344 | -0.091562
| 640 | 1.4112 | 1.0976 | -0.42571 | -0.10889
| 650 | 1.4332 | 1.1147 | -0.44799 | -0.12621
| 660 | 1.4553 | 1.1319 | -0.47027 | -0.14354
| 670 | 1.4773 | 1.149 | -0.49254 | -0.16087
| 680 | 1.4994 | 1.1662 | -0.51482 | -0.17819
| 690 | 1.5214 | 1.1833 | -0.5371 | -0.19552
| 700 | 1.5435 | 1.2005 | -0.55937 | -0.21285
| 710 | 1.5655 | 1.2176 | -0.58165 | -0.23017
| 720 | 1.5876 | 1.2348 | -0.60393 | -0.2475
| 730 | 1.6097 | 1.2519 | -0.6262 | -0.26483
| 740 | 1.6317 | 1.2691 | -0.64848 | -0.28215
| 750 | 1.6538 | 1.2862 | -0.67076 | -0.29948
| 760 | 1.6758 | 1.3034 | -0.69304 | -0.31681
| 770 | 1.6978 | 1.3205 | -0.71531 | -0.33413
| 780 | 1.7199 | 1.3377 | -0.73759 | -0.35146
| 790 | 1.7419 | 1.3548 | -0.75987 | -0.36878
| 800 | 1.764 | 1.372 | -0.78214 | -0.38611
| 810 | 1.786 | 1.3891 | -0.80442 | -0.40344
| 820 | 1.8081 | 1.4063 | -0.8267 | -0.42076
| 830 | 1.8301 | 1.4234 | -0.84897 | -0.43809
| 840 | 1.8522 | 1.4406 | -0.87125 | -0.45542
| 850 | 1.8742 | 1.4577 | -0.89353 | -0.47274
| 860 | 1.8963 | 1.4749 | -0.9158 | -0.49007
| 870 | 1.9183 | 1.492 | -0.93808 | -0.5074
| 880 | 1.9404 | 1.5092 | -0.96036 | -0.52472
| 890 | 1.9625 | 1.5263 | -0.98263 | -0.54205
| 900 | 1.9845 | 1.5435 | -1.0049 | -0.55937
| 910 | 2.0065 | 1.5606 | -1.0272 | -0.5767
| 920 | 2.0286 | 1.5778 | -1.0495 | -0.59403
| 930 | 2.0507 | 1.5949 | -1.0717 | -0.61135
| 940 | 2.0727 | 1.6121 | -1.094 | -0.62868
| 950 | 2.0947 | 1.6292 | -1.1163 | -0.64601
| 960 | 2.1168 | 1.6464 | -1.1386 | -0.66333
| 970 | 2.1389 | 1.6635 | -1.1608 | -0.68066
| 980 | 2.1609 | 1.6807 | -1.1831 | -0.69799
| 990 | 2.1829 | 1.6978 | -1.2054 | -0.71531
| 1000 | 2.205 | 1.715 | -1.2277 | -0.73264

## METHANOL_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/PJ out | PJ/PJ out | Factor | years | PJ/GW | M€ /GW or M€/Pja | M€ /GW or M€/Pja | M€ /PJ | years
METH_ship | METH ship |  | METH | EXP_METH |  | 2020 | 2030 | 0.55446 |  |  | 0.95 | 20 | 1 | 0.38947 | 0.0021192 |  |  | ~FI_Process
[6 empty] | 2030 |  | 0.55446 |  |  | 0.95 | 20 | 1 | 0.38947 | 0.0021192 |  |  | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
[6 empty] | 2050 |  | 0.65347 |  |  | 0.95 | 20 | 1 | 0.38947 | 0.0021192 |  |  | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
*
[18 empty] | PRE | METH_ship | METH ship | PJ | Pja | DAYNITE | EXP_METH | YES
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## JET FUEL
NO PIPES?? | SHIPS
| NO KM?? |  |  |  |  | JET FUEL=LHC in technology cathalogue
| Technical life time [years] | 20
Jet fuel
[6 empty] | 11.95 | kwh/kg
|  | 2030 and 2050 | 2050 |  |  | 11.95 | MWh/t
| LHC: Energy demand [MJ/km] | 2205 | 1715 |  |  | 11.95 | mw/t | 0.01195 | GW/T
| LHC: Investment cost [EUR/tonLHC] | 780.2255 |  |  |  | 0.01195 | MWh/kg
| LHC: Fixed O&M cost [EUR/tonLHC/y] | 4.2535
| LHC: Port cost [EUR/tonLHC] | 1.4887
| LHC: Energy demand [pJ/km] | 0.002205 | 0.001715
| LHC: Investment cost [MEUR/PJ] | 18.1363 |  |  |  | MWh-->pj |  |  | Typical ship
| LHC: Fixed O&M cost [MEUR/PJ/y] | 0.098872 |  |  |  | 3.6e-06 |  |  | 45000 | tons
| LHC: Port cost [MEUR/PJ] | 0.034605
1.9359
| Distance (km) |  |  | EFFICIENCY 2030 | EFFICIENCY 2050
| 10 | 0.02205 | 0.01715
| 20 | 0.0441 | 0.0343
| 30 | 0.06615 | 0.05145
| 40 | 0.0882 | 0.0686
| 50 | 0.11025 | 0.08575
| 60 | 0.1323 | 0.1029
| 70 | 0.15435 | 0.12005
| 80 | 0.1764 | 0.1372
| 90 | 0.19845 | 0.15435
| 100 | 0.2205 | 0.1715
| 110 | 0.24255 | 0.18865
| 120 | 0.2646 | 0.2058
| 130 | 0.28665 | 0.22295
| 140 | 0.3087 | 0.2401
| 150 | 0.33075 | 0.25725
| 160 | 0.3528 | 0.2744
| 170 | 0.37485 | 0.29155
| 180 | 0.3969 | 0.3087
| 190 | 0.41895 | 0.32585
| 200 | 0.441 | 0.343
| 210 | 0.46305 | 0.36015
| 220 | 0.4851 | 0.3773
| 230 | 0.50715 | 0.39445
| 240 | 0.5292 | 0.4116
| 250 | 0.55125 | 0.42875
| 260 | 0.5733 | 0.4459
| 270 | 0.59535 | 0.46305
| 280 | 0.6174 | 0.4802
| 290 | 0.63945 | 0.49735
| 300 | 0.6615 | 0.5145
| 310 | 0.68355 | 0.53165
| 320 | 0.7056 | 0.5488
| 330 | 0.72765 | 0.56595
| 340 | 0.7497 | 0.5831
| 350 | 0.77175 | 0.60025
| 360 | 0.7938 | 0.6174
| 370 | 0.81585 | 0.63455
| 380 | 0.8379 | 0.6517
| 390 | 0.85995 | 0.66885
| 400 | 0.882 | 0.686
| 410 | 0.90405 | 0.70315
| 420 | 0.9261 | 0.7203
| 430 | 0.94815 | 0.73745
| 440 | 0.9702 | 0.7546
| 450 | 0.99225 | 0.77175
| 460 | 1.0143 | 0.7889
| 470 | 1.0363 | 0.80605
| 480 | 1.0584 | 0.8232
| 490 | 1.0804 | 0.84035
| 500 | 1.1025 | 0.8575
| 510 | 1.1245 | 0.87465
| 520 | 1.1466 | 0.8918
| 530 | 1.1686 | 0.90895
| 540 | 1.1907 | 0.9261
| 550 | 1.2127 | 0.94325
| 560 | 1.2348 | 0.9604
| 570 | 1.2569 | 0.97755
| 580 | 1.2789 | 0.9947
| 590 | 1.301 | 1.0118
| 600 | 1.323 | 1.029
| 610 | 1.345 | 1.0461
| 620 | 1.3671 | 1.0633
| 630 | 1.3891 | 1.0804
| 640 | 1.4112 | 1.0976
| 650 | 1.4332 | 1.1147
| 660 | 1.4553 | 1.1319
| 670 | 1.4773 | 1.149
| 680 | 1.4994 | 1.1662
| 690 | 1.5214 | 1.1833
| 700 | 1.5435 | 1.2005
| 710 | 1.5655 | 1.2176
| 720 | 1.5876 | 1.2348
| 730 | 1.6097 | 1.2519
| 740 | 1.6317 | 1.2691
| 750 | 1.6538 | 1.2862
| 760 | 1.6758 | 1.3034
| 770 | 1.6978 | 1.3205
| 780 | 1.7199 | 1.3377
| 790 | 1.7419 | 1.3548
| 800 | 1.764 | 1.372
| 810 | 1.786 | 1.3891
| 820 | 1.8081 | 1.4063
| 830 | 1.8301 | 1.4234
| 840 | 1.8522 | 1.4406
| 850 | 1.8742 | 1.4577
| 860 | 1.8963 | 1.4749
| 870 | 1.9183 | 1.492
| 880 | 1.9404 | 1.5092
| 890 | 1.9625 | 1.5263
| 900 | 1.9845 | 1.5435
| 910 | 2.0065 | 1.5606
| 920 | 2.0286 | 1.5778
| 930 | 2.0507 | 1.5949
| 940 | 2.0727 | 1.6121
| 950 | 2.0947 | 1.6292
| 960 | 2.1168 | 1.6464
| 970 | 2.1389 | 1.6635
| 980 | 2.1609 | 1.6807
| 990 | 2.1829 | 1.6978
| 1000 | 2.205 | 1.715

## Jetfuel_TRANSPORT
~FI_T
TechName | TechDesc | Comm-IN-A | Comm-IN | Comm-OUT | Comm-OUT-A | Year | START | EFF | Input | Output | AFA | Life | CAP2ACT | INVCOST | FIXOM | VAROM | ILED
\I:Technology Name | Technology Description | Auxiliary Input Commodity | Input Commodity | Output Commodity | Auxiliary Output Commodity |  |  | Technical Efficiency | Fuel input level | Fuel Output level | Annual Availability Factor | Lifetime of Process | Capacity to Activity Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Construction time
\I: Units | [7 empty] | PJ out/PJ in | PJ/PJ out | PJ/PJ out | Factor | years | PJ/GW | M€ /GW or M€/Pja | M€ /GW or M€/Pja | M€ /PJ | years
KRE_ship | KRE ship |  | KRE | EXP_KRE |  | 2020 | 2030 | 1 |  |  | 0.95 | 20 | 1 | 0.19913 | 0.0010835 |  |  | ~FI_Process
|  | HFO |  |  |  | 2020 |  |  | 0.1 | [8 empty] | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
|  |  | KRE | EXP_KRE |  | 2030 |  | 1 |  |  | 0.95 | 20 | 1 | 0.19913 | 0.0010835 |  |  | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
|  | HFO |  |  |  | 2030 |  |  | 0.1 | [8 empty] | *
|  |  | KRE | EXP_KRE |  | 2050 |  | 1 |  |  | 0.95 | 20 | 1 | 0.19913 | 0.0010835 |  |  | PRE | KRE_ship | KRE ship | PJ | Pja | DAYNITE | EXP_KRE | YES
|  | HFO |  |  |  | 2050 |  |  | 0.1
Note on Y4: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on AC4: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on AD4: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE4: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on AF4: Allowed Ctype ELC (Electricity)
Note on E8: Comm-IN-A indicates an auxillary input, thus not consider with respect the efficiency
Note on H8: Comm-OUT-A indicates an auxillary output, thus not consider with respect the efficiency
Note on AD12: Allowed TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AE12: Amit Kanudia: Needed only when one wants to override the VEDA default assignment
Note on AF12: Allowed Vintage NO (if empty by default mean NO) YES
Note on Y13: Sets declarations are inherited. Allowed Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) STGIPS (Pump Storage IP) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## 111 1 el Main distri50-60kVcabl
Technology |  | Energy Transport Electricity Main distribution, electricity cables
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref | I need arounf 300 kv
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines 20-100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines above 100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 1 [%] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 2 [%] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S]
| Auxiliary electricity consumption [%] of energy transmitted | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S] | 4
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 50 | C | 5
| Typical load profile (-) | 45% | 45% | 45% | 45% | 45% | 45% | 42.3% | 54% | D
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 5 | 1 | 5 | E
Financial data
| Investment costs; single line, 0 - 50 MW [EUR/MW/m] | 6.3802 | 6.3802 | 6.3802 | 6.3802 | 6.1061 | 6.7846 | 5.8438 | 7.2145 | [F, G] | [6, 7]
| Investment costs; single line, 50-100 MW [EUR/MW/m] | 4.1472 | 4.1472 | 4.1472 | 4.1472 | 3.969 | 4.41 | 3.7984 | 4.6894 | [H, G] | [6, 7]
| Investment costs; single line, 100 - 250 MW [EUR/MW/m] | 3.2965 | 3.2965 | 3.2965 | 3.2965 | 3.1548 | 3.5054 | 3.0193 | 3.7275 | [I, G] | [6, 7]
| Investment costs; single line, 250-500 MW [EUR/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 6
| Investment costs; single line, 500-1000 MW [EUR/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 7
| Investment costs; single line, above 1000 MW [EUR/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 8
| Reinforcement costs [EUR/MW] | 16801.2889 | 16801.2889 | 16801.2889 | 16801.2889 | 17044.1948 | 17866.0323 | 17290.6125 | 18998.2513 | [K, O] | 6
| Investment costs; type 1 station [EUR/MW] | 80816.3266 | 80816.3266 | 80816.3266 | 80816.3266 | 81984.7345 | 85937.8768 | 83170.0348 | 91383.9937 | [L, O] | 8
| Investment costs; type 2 station [EUR/MW] | 4759.6563 | 4759.6563 | 4759.6563 | 4759.6563 | 4828.4694 | 5061.2886 | 4898.2773 | 5382.0363 | [M, O]
| Investments, percentage installation | 42% | 42% | 42% | 42% | 37.37% | 42% | 32.96% | 42% | P | 6
| Investments, percentage materials | 58% | 58% | 58% | 58% | 58% | 62.63% | 58% | 67.04% | P | 6
| Fixed O&M [EUR/MW/km/year] | 24.9898 | 26.2015 | 27.4719 | 28.8039 | 26.0952 | 26.5735 | 25.1642 | 26.5735 | Q | 9
| Variable O&M [EUR/MWh/km] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R
Technology-specific data
References:
1. U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
2. energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
3. Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
4. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
5. Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. PEX Guiden, Ericsson
8. Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
B. Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing transfer and thus increasing losses. The uncertainty span for 2020 mainly takes changes in power transfer into account, where the lower bound corresponds to a reduction of power transfer to a 1998 level, and the upper bound corresponds to a continued increase in losses stemming from increased power transfer. Technology development with introduction of e.g. super conducting transformers and super conducting power lines could lead to reduced losses on transmission level. Other factors, such as load control/optimization could also reduce losses in generators due to increased load factor. This technology development is not anticipated to have effect before 2020, but is possible in a second upgrade of electricity system in 2050.
C. Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development on cable materials is anticipated to give an increase in cable life length. This in combination with low thermal loadings could give life length of up to 50 years in the future.
D. Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 20%.
E. Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
F. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. For power range 0 - 50 MW the costs is calculated as the average cost of two cables types with cross section areas 240 mm2 and 630 mm2,, corresponding to power levels of 20-35 MW and 50-60 MW respectively. The cost per MV decreases with increasing power level. The interval 20-35 MW has a cost of 6,7 EUR/MW/m and the interval 50-60 MW a cost of 4,2 EUR/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9. Power level below 20MW is not considered for this voltage level.
G. Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
H. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For power range 50-100 MW the costs is calculated as the average cost for three cables with cross section areas 630 mm2, 800mm2 and 1000 mm2, corresponding to power levels of 50-60 MW, 69 MW and 76 MW respectively. The cost per MV decreases with increasing power level. The power interval 50-60 MW has a cost of 4,2 EUR/MW/m, at power level of 69 MW the cost is 3,6 EUR/MW/m and at the power level 76 the cost is 3,4 EUR/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9.
I. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the costs is given for a cable with cross section area of 1200 mm2, corresponding to a power level of 100 MW. Power levels above 100 MW are not considered for this voltage level.
J. Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable reduced with 60 800 EUR per kilometer.
K. Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18 - 20 and depends on power level and cable length.
L. Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span 20 - 126 MW: Station cost (EUR) = 16 000 (EUR/MW) x Power rating (MW) + 2 350 000 (EUR). Using a single transformer instead of two reduces the cost by a factor 0,86 - 0,87.
M. Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
O. Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
P. The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
Q. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no maintenaince on cables. The O&M cost is assumed to be reduced over time by an annual factor of 1 - 1,8% due to increased efficiency. Upper uncertainty bounds for 2020 and 2050 corresponds to no efficiency increase in O&M and lower bounds corresponds to a continuous annual efficiency increase of 1,8%
R. Variable O&M cost is in very low for electric transmission systems and considered to be negligible
S. Energy losses and auxiliary electricity consumption can be considered negligible

## H2 140
Technology |  | Main distribution line H2 - 140 bar
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-100 MW, [%/1000 km] | 7.5 | 7 | 6.3 | 6.2 | 12.3 | 5.5 | 10.3 | A
| Energy losses, lines 100-250 MW, [%/1000 km] | 6.4 | 5.9 | 5.3 | 5.2 | 10.4 | 4.6 | 8.7 | A
| Energy losses, lines 250-500 MW, [%/1000 km] | 5.1 | 4.7 | 4.2 | 4.1 | 8.3 | 3.7 | 6.9 | A
| Energy losses, lines 500-1500 MW, [%/1000 km] | 3.8 | 3.5 | 3.1 | 3.1 | 6.2 | 2.7 | 5.2 | A
| Energy losses, lines 1500-5000 MW, [%/1000 km] | 2.7 | 2.5 | 2.2 | 2.2 | 4.3 | 1.9 | 3.6 | A
| Energy losses, lines 5000-20000 MW, [%/1000 km] | 2.1 | 1.9 | 1.7 | 1.7 | 3.4 | 1.5 | 2.8 | A
| Energy losses, lines >20000 MW, [%/1000 km] | 1.5 | 1.4 | 1.3 | 1.3 | 2.5 | 1.1 | 2.1 | A
| Energy demand, compressor filling station [% | 2.1 | 1.68 | 1.47 | 1.47 | 3.7 | 0.9 | 2.5 | B
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 0 - 100 MW [EUR/MW/m] | 4.3598 | 4.1472 | 3.9345 | 3.9345 | 5.5295 | 3.5091 | 4.9979 | C | 0
| Investment costs; single line, 100 - 250 MW [EUR/MW/m] | 1.9141 | 1.8077 | 1.7014 | 1.7014 | 2.4458 | 1.5951 | 2.2331 | C | 0
| Investment costs; single line, 250-500 MW [EUR/MW/m] | 1.1697 | 1.1697 | 1.0634 | 1.0634 | 1.4887 | 0.95704 | 1.3824 | C | 0
| Investment costs; single line, 500-1000 MW [EUR/MW/m] | 0.8507 | 0.74436 | 0.74436 | 0.74436 | 0.95704 | 0.63802 | 0.95704 | C | 0
| Investment costs; single line, 1000-4000 MW [EUR/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.42535 | 0.53169 | 0.42535 | 0.53169 | C | 0
| Investment costs; single line, above 6000 MW [EUR/MW/m] | 0.24458 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | C | 0
| Investments, percentage installation [%] | 77.5% | 77.5% | 77.5% | 75% | 80% | 70% | 80% | D | 0
| Investments, percentage materials [%] | 22.5% | 22.5% | 22.5% | 20% | 25% | 20% | 30% | D | 0
| Fixed O&M [EUR/km/year/MW] | 0.54232 | 0.26584 | 0.19938 | 0.21267 | 1.0634 | 0.11697 | 1.0634 | E | 0
| Variable O&M [EUR/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. Curently, the optimum seems to be: velosity (m/s)≈4.4*Q^0.1, dPdL(bar/km)≈1.28*Q^(-0.75), Q=energy flow (MW)
B. Energy to compress from 35 barg to 140 barg. This value can be lowered by only compress to curent operation pressure in transmission line using outtake from interstages compressors
C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
D. Installation cost is ~80% for small pipes and ~75% for large pipes
E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
References:
<none>

## NH3_DATA_PIPE
Technology |  | Main distribution line - NH3
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses [‰] | <0.1 | <0.1 | <0.1 | 0.01 | 0.1 | 0.01 | 0.1 | [A, B]
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 1-15 MW [EUR/MW/m] | 10.7401 | 10.2084 | 9.783 | 9.6502 | 16.0837 | 8.8107 | 13.7055 | [B, C] | 0
| Investment costs; single line, 15-30 MW [EUR/MW/m] | 7.1246 | 6.8056 | 6.4866 | 6.413 | 10.6883 | 5.855 | 9.1078 | [B, C] | 0
| Investment costs; single line, 30-100 MW [EUR/MW/m] | 2.9774 | 2.8711 | 2.6584 | 2.6629 | 4.4382 | 2.4313 | 3.782 | [B, C] | 0
| Investment costs; single line, 100-300 MW [EUR/MW/m] | 1.3824 | 1.276 | 1.276 | 1.215 | 2.025 | 1.1093 | 1.7256 | [B, C] | 0
| Investment costs; single line, 300-500 MW [EUR/MW/m] | 0.74436 | 0.74436 | 0.74436 | 0.69785 | 1.1631 | 0.63714 | 0.9911 | [B, C] | 0
| Investment costs; single line, 500-1000 MW [EUR/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.42205 | 0.70341 | 0.38533 | 0.5994 | [B, C] | 0
| Investment costs; single line, 1000-2000 MW [EUR/MW/m] | 0.31901 | 0.21267 | 0.21267 | 0.2424 | 0.404 | 0.22131 | 0.34427 | [B, C] | 0
| Investment costs; single line, above 2000 MW [EUR/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.19257 | 0.32095 | 0.17582 | 0.27349 | [B, C] | 0
| Investments, percentage installation [%] | 87% | 82.65% | 78.3% | 80% | 90% | 75% | 90% | D | 0
| Investments, percentage materials [%] | 13% | 17.35% | 21.7% | 10% | 20% | 10% | 25% | C | 0
| Fixed O&M [EUR/km/year] | 106.3373 | 106.3373 | 106.3373 | 53.1686 | 212.6745 | 53.1686 | 212.6745 | E | 0
| Variable O&M [EUR/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data

## Ship Transport
Technology |  | Ship transport
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| LH2: Energy demand [MJ/km] | Est: 2250; Est: 2025; Est: 1575; -: [A, F]
| L20: Energy demand [MJ/km] | Est: 2450; Est: 2205; Est: 1715; -: [A, F]
| LHC: Energy demand [MJ/km] | Est: 2450; Est: 2205; Est: 1715; -: [A, F]
| Technical life time [years] | Est: 20; Est: 20; Est: 20; -: 1
Financial data
| LH2 Investment cost [EUR/tonH2] | 15950.5908 | 14887.2181 | 10633.7272 | 0 | 0 | 0 | 0 | G | [2, 3]
| L20: Investment cost [EUR/tonL20] | 1860.9023 | 1978.8327 | 1978.8327 | 0 | 0 | 0 | 0 | [B, C] | [2, 3]
| LHC: Investment cost [EUR/tonLHC] | 733.7272 | 780.2255 | 780.2255 | 0 | 0 | 0 | 0 | D | 0
| LH2: Fixed O&M cost [EUR/tonH2/y] | 79.753 | 74.4361 | 53.1686 | 0 | 0 | 0 | 0 | E | 0
| L20:Fixed O&M cost [EUR/tonL20/y] | 9.5704 | 9.5704 | 9.5704 | 0 | 0 | 0 | 0 | E | 0
| LHC: Fixed O&M cost [EUR/tonLHC/y] | 4.2535 | 4.2535 | 4.2535 | 0 | 0 | 0 | 0 | E | 0
| LH2: Port cost [EUR/tonH2] | 7.2309 | 6.3802 | 4.2535 | 0 | 0 | 0 | 0 | 0 | 3.1901
| L20: Port cost [EUR/tonH2] | 1.8077 | 1.8077 | 1.8077 | 0 | 0 | 0 | 0 | 0 | 3.1901
| LHC: Port cost [EUR/tonLHC] | 1.4887 | 1.4887 | 1.4887 | 0 | 0 | 0 | 0 | 0 | 3.1901
Technology-specific data
References:
1. The Basics of the Tanker Shipping Market, Euronav, 2017
2. Torm annual report 2018
3. Shipping CO₂ - UK cost estimation study, 2018
Notes:
A. Energy based on fuel LHV which is approximated by: 0.023*Mcargo+1400 for L20 and LHC. For LH2 the weight of the cargo is much less (do to the low weight of H2) why the weight of the entire ship have been used instead
B. Investment cost based on: Cost [€/t] = 4000 - 0.05*Mcargo, where Mcargo is design capacity of ship
C. CAPEX of LPG carrier see https://www.seatrade-maritime.com/tankers/euronav-buys-another-scrubber-fitted-resale-vlcc-newbuild
D. CAPEX of tanker see BRS group annual review 2019
E. Fixed O&M is assumed to be ~5% of annual CAPEX
F. It is assumed that the efficiency of the combustion engine is improved so it is 90% in 2030 and 70% in 2050 of the efficiency in 2020. The 70% is based on the difference between the efficiency of a traditional combustion engine and a fuel cell engine. The 90% is based on natural replacement of old tankers with news tankers that have a more efficient engine (some of them might be fuel cells) and revamp of existing engines
G. Assumed cost reduction after LH2 tanker is commercialized

## CO2 PIPELINE
Technology |  | CO2 pipeline transport
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.5 | 1.5 |  | 1
Financial data
| Investment costs; onshore pipeline, gas phase, 10 t CO₂/h [EUR/(tCO2/h)/m] | 130 | 130 | 130 | 130 | 130 | 104 | 169 | 104 | 169 | A | 2
| Investment costs; onshore pipeline, dense phase, 30 t CO₂/h [EUR/(tCO2/h)/m] | 43 | 43 | 43 | 43 | 43 | 34 | 56 | 34 | 56 | A | 2
| Investment costs; onshore pipeline, dense phase, 80 t CO₂/h [EUR/(tCO2/h)/m] | 18 | 18 | 18 | 18 | 18 | 14 | 23 | 14 | 23 | A | 2
| Investment costs; onshore pipeline, dense phase, 120 t CO₂/h [EUR/(tCO2/h)/m] | 13 | 13 | 13 | 13 | 13 | 10 | 17 | 10 | 17 | A | 2
| Investment costs; offhore single line, 120 t CO₂/h [EUR/(tCO2/h)/m] | 33 | 33 | 33 | 33 | 33 | 26 | 43 | 26 | 43 | B | 2
| Fixed O&M [EUR/(tCO2/h)/year/km] | 20 | 20 | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3
Variable O&M [EUR/(tCO2/h)/km] | bar: -
Technology specific data
References:
1. Technology Catalogue Natural gas Main Distribution Lines, Table 6
2. COWI estimate 2023
3. The Costs of CO₂ transport, Zero Emission Platform (ZEP), Report 2010
Notes:
A. Estimate includes cost for permitting, landowner compensation, soil works, cathodic protection and coating. Sectionalisation valve assumed every 15 km. Installation costs are based om experienced cost for NG pipeline installation in Denmark. The 10 t CO2/h gas phase and 30 t CO2/h dense phase capacity are based on cost of a 6" pipeline. The 80 t CO2/h is based on cost of a 8" pipeline. The 120 t CO2/h is based on cost of a 10" pipeline.
B. Offshore pipeline installation is more costly than onshore pipeline.
C. Operating cost is assumed to be fixed for each pipeline. Estimate is based on cost of 12" pipeline in [2] and excludes pumping/compression cost.
D. Variable O&M are negigible.

## CO2 SHIP
Technology |  | CO₂ ship transportation
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy demand, 4,000 t CO₂ ship (MWh/day) | 90 | 90 | 80 | 80 | 200 | 60 | 160 | A | 1
| Energy demand, 10,000 t CO₂ ship (MWh/day) | 180 | 180 | 150 | 160 | 280 | 140 | 240 | A | 1
| Technical life time CO₂ carrier [years] | ctrl: 40; ctrl: 40; ctrl: 40; -: 2
| Construction time [years] | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5
Financial data
| Investments, 4000 t CO₂ ship (EUR/t CO₂) | 9560 | 9082 | 7648 | 6692 | 12428 | 4780 | 9560 | B | 2.868
| Investments,10,000 t CO2 ship (EUR/t CO₂) | 6214 | 5927.2 | 4780 | 4780 | 6214 | 2868 | 6214 | B | 2.868
| Fixed O&M 4000 t CO₂ Ship (EUR/t CO₂/year) | 456.968 | 434.1196 | 365.5744 | 319.8776 | 594.0584 | 228.484 | 456.968 | C | 2.868
| Fixed O&M 10000 t CO₂ Ship (EUR/t CO₂/year) | 297.0292 | 283.3202 | 228.484 | 228.484 | 297.0292 | 137.0904 | 297.0292 | C | 2.868
| Variable O&M 4000 t CO₂ ship (EUR/[t CO₂]) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D | 0
| Variable O&M 14000 t CO₂ ship (EUR/[t CO₂/h]/) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D | 0
Technology-specific data
References:
1. Based on input from Knutsen shipping
2. The Cost of CO₂ Transport – Post-demonstration CCS in the EU. ZEP report 2010
3. Shipping CO₂ - UK cost estimation study. ElementEnergy, Final report for Business, Energy & Industrial Strategy Department, Nov 2018.
Notes:
A. Energy consumption based on fuel LHV at cruising speed 15 knots or 28 km/h and average of full and empty cargo. Typical LHV of Heavy Fuel Oil (HFO) is 40.4 MJ /kg.
B. Ship cost is based on CO₂ pressure conditions of 15 bara, -25°C. Significantly lower cost is reported in literature for low pressure 7 bara and -50°C, however no experience exists with transportation of CO₂ at these conditions.
C. Fixed O&M of ships is taken as 5% of CAPEX incl. Pilot assistance and docking fee to harbor
D. Variable O&M exlcuding fuel costs is assumed to be insignificant. Tax on tonnage of CO₂ shipped is also excluded as this will be highly dependent on the specific port.