## Commodities
~FI_Comm
Csets | CommName | CommDesc | Unit | LimType | CTSLvl | PeakTS | Ctype
\I:Commodity Set Membership | Commodity Name | Commodity Description | Unit | Sense of the Balance EQN. | Timeslice Level | Peak Monitoring | Electricity Indicator
\I:
NRG | GRDSTOLIONONELCMIDN0_IN | Power In | PJ | FX | DAYNITE |  | ELC
NRG | GRDSTOLIONONELCMIDN0_OUT | Power Out | PJ | FX | DAYNITE |  | ELC
NRG | GRDSTOHSTNONH2XTRMN0_IN | Power In | PJ | FX | DAYNITE
NRG | GRDSTOHSTNONH2XTRMN0_OUT | Power Out | PJ | FX | DAYNITE
NRG | GRDSTOHSTNONH3XTRMN0_IN | Power In | PJ | FX | DAYNITE
NRG | GRDSTOHSTNONH3XTRMN0_OUT | Power Out | PJ | FX | DAYNITE
NRG | GRDSTOHSTNOCH3OHXTRMN0_IN | Power In | PJ | FX | DAYNITE
NRG | GRDSTOHSTNOCH3OHXTRMN0_OUT | Power Out | PJ | FX | DAYNITE
NRG | GRDSTOHSTNOKREXTRMN0_IN | Power In | PJ | FX | DAYNITE
NRG | GRDSTOHSTNOKREXTRMN0_OUT | Power Out | PJ | FX | DAYNITE
NRG | GRDSTOHSTNOCO2XTRMN0_IN | Power In | kt | FX | DAYNITE
NRG | GRDSTOHSTNOCO2XTRMN0_OUT | Power Out | kt | FX | DAYNITE
Note on B3: Csets declarations are inherited until the next one is encountered. Allowed Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on F3: Amit Kanudia: LO for PRODUCTION >= CONSUMPTION (Default) FX for PRODUCTION = CONSUMPTION UP for PRODUCTION <= CONSUMPTION
Note on G3: Allowed CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on H3: Allowed PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on I3: Allowed Ctype ELC (Electricity)

## Processes
~FI_Process | [7 empty] | ~FI_T
Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage | TechName | *TechDesc | Comm-IN | Comm-IN-A | Comm-OUT | CAP2ACT | START | INPUT~2030 | INPUT~2040 | INPUT~2050 | LIFE~2030 | LIFE~2040 | LIFE~2050 | STG_MAXCYC~2030 | STG_MAXCYC~2040 | STG_MAXCYC~2050 | STG_CHRG | EFF~2030 | EFF~2040 | EFF~2050 | STG_EFF~2030 | STG_EFF~2040 | STG_EFF~2050 | TEMP~2030 | TEMP~2040 | TEMP~2050 | STG_LOSS~2030 | STG_LOSS~2040 | STG_LOSS~2050 | AF~LO | INVCOST~2030 | INVCOST~2040 | INVCOST~2050 | FIXOM~2030 | FIXOM~2040 | FIXOM~2050 | VAROM~2030 | VAROM~2040 | VAROM~2050 | ILED~2030 | ILED~2040 | ILED~2050 | PKNO | Peak
\I: Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking | \I: Technology Name | Technology Description | Primary input fuels | Auxiliary input fuels | Primary output fuels |  | Start year of investment | Input level relative to process activity | Input level relative to process activity | Input level relative to process activity | Techincal lifetime | Techincal lifetime | Techincal lifetime | Maximum number of storage cycles over lifetime | Maximum number of storage cycles over lifetime | Maximum number of storage cycles over lifetime | State of charge at beginning and end of each period | Efficiency | Efficiency | Efficiency | Storage efficiency | Storage efficiency | Storage efficiency | Water temperature of heat storages | Water temperature of heat storages | Water temperature of heat storages | Annual storage loss | Annual storage loss | Annual storage loss | Minimum storage level | Total investment cost | Total investment cost | Total investment cost | Annual fixed O&M cost | Annual fixed O&M cost | Annual fixed O&M cost | Variable O&M cost | Variable O&M cost | Variable O&M cost | Construction time | Construction time | Construction time | Peak contribution | Contribution to PEAK share
\I: | [7 empty] | \I: Units | [5 empty] | Year | Factor | Factor | Factor | Years | Years | Years | Cycles | Factor | Factor | TJ | Factor | Factor | Factor | Factor | Factor | Factor | Deg. C | Deg. C | Deg. C | Factor | Factor | Factor | TJ | MEUR/GW or MEUR/Pja | MEUR/GW or MEUR/Pja | MEUR/GW or MEUR/Pja | MEUR/GW or MEUR/Pja | MEUR/GW or MEUR/Pja | MEUR/GW or MEUR/Pja | MEUR/PJ | MEUR/PJ | MEUR/PJ | years | years | years | Yes (1) or No (0) | Factor
PRE | GRDSTOHSTNONH2XTRMN0_PI | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Power In | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNONH2XTRMN0_PI | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Power In | H2 | ELC | GRDSTOHSTNONH2XTRMN0_IN | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 25 | 30 | 30 |  |  |  |  | 0.88 | 0.88 | 0.88 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOHSTNONH2XTRMN0_E | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Energy | PJ | PJa | DAYNITE |  | YES | GRDSTOHSTNONH2XTRMN0_E | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Energy | GRDSTOHSTNONH2XTRMN0_IN |  | GRDSTOHSTNONH2XTRMN0_OUT | 1 | 2030 |  |  |  | 25 | 30 | 30 | [13 empty] | -3.65 | -3.65 | -3.65 |  | 13265.915 | 7990.3876 | 6203.1667 | [6 empty] | 0.5 | 0.4 | 0.4 | 0
PRE | GRDSTOHSTNONH2XTRMN0_PO | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Power Out | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNONH2XTRMN0_PO | Grid Storage Hydrogen Storage - Tanks Hydrogen Blend Transmission New 0 - Power Out | GRDSTOHSTNONH2XTRMN0_OUT | ELC | H2 | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 25 | 30 | 30 |  |  |  |  | 1 | 1 | 1 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | 0.5317 | 0.5317 | 0.42536 | [6 empty] | 1 | 1
PRE | GRDSTOHSTNONH3XTRMN0_PI | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Power In | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNONH3XTRMN0_PI | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Power In | AMM | ELC | GRDSTOHSTNONH3XTRMN0_IN | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOHSTNONH3XTRMN0_E | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Energy | PJ | PJa | DAYNITE |  | YES | GRDSTOHSTNONH3XTRMN0_E | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Energy | GRDSTOHSTNONH3XTRMN0_IN |  | GRDSTOHSTNONH3XTRMN0_OUT | 1 | 2030 |  |  |  | 20 | 20 | 25 | [13 empty] | -3.65 | -3.65 | -3.65 |  | 393.7008 | 393.7008 | 393.7008 |  |  |  | 19.685 | 19.685 | 19.685 | 0.5 | 0.4 | 0.4 | 0
PRE | GRDSTOHSTNONH3XTRMN0_PO | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Power Out | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNONH3XTRMN0_PO | Grid Storage Ammonia Storage - Tanks Ammonia Blend Transmission New - Power Out | GRDSTOHSTNONH3XTRMN0_OUT | ELC | AMM | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 1 | 1
PRE | GRDSTOHSTNOCH3OHXTRMN0_PI | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Power In | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNOCH3OHXTRMN0_PI | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Power In | METH | ELC | GRDSTOHSTNOCH3OHXTRMN0_IN | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOHSTNOCH3OHXTRMN0_E | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Energy | PJ | PJa | DAYNITE |  | YES | GRDSTOHSTNOCH3OHXTRMN0_E | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Energy | GRDSTOHSTNOCH3OHXTRMN0_IN |  | GRDSTOHSTNOCH3OHXTRMN0_OUT | 1 | 2030 |  |  |  | 20 | 20 | 25 | [13 empty] | -3.65 | -3.65 | -3.65 |  | 253.1646 | 253.1646 | 253.1646 |  |  |  | 12.6582 | 12.6582 | 12.6582 | 0.5 | 0.4 | 0.4 | 0
PRE | GRDSTOHSTNOCH3OHXTRMN0_PO | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Power Out | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNOCH3OHXTRMN0_PO | Grid Storage Methanol Storage - Tanks Methanol Blend Transmission New - Power Out | GRDSTOHSTNOCH3OHXTRMN0_OUT | ELC | METH | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 1 | 1
PRE | GRDSTOHSTNOKREXTRMN0_PI | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Power In | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNOKREXTRMN0_PI | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Power In | KRE | ELC | GRDSTOHSTNOKREXTRMN0_IN | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOHSTNOKREXTRMN0_E | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Energy | PJ | PJa | DAYNITE |  | YES | GRDSTOHSTNOKREXTRMN0_E | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Energy | GRDSTOHSTNOKREXTRMN0_IN |  | GRDSTOHSTNOKREXTRMN0_OUT | 1 | 2030 |  |  |  | 20 | 20 | 25 | [13 empty] | -3.65 | -3.65 | -3.65 |  | 193.7084 | 193.7084 | 193.7084 |  |  |  | 9.6854 | 9.6854 | 9.6854 | 0.5 | 0.4 | 0.4 | 0
PRE | GRDSTOHSTNOKREXTRMN0_PO | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Power Out | PJ | GW | DAYNITE |  | YES | GRDSTOHSTNOKREXTRMN0_PO | Grid Storage JetFuel Storage - Tanks JetFuel Blend Transmission New - Power Out | GRDSTOHSTNOKREXTRMN0_OUT | ELC | KRE | 31.536 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 1 | 1
PRE | GRDSTOHSTNOCO2XTRMN0_PI | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Power In | kt | kta | DAYNITE |  | YES | GRDSTOHSTNOCO2XTRMN0_PI | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Power In | CO2 | ELC | GRDSTOHSTNOCO2XTRMN0_IN | 1 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOHSTNOC02XTRMN0_E | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Energy | kt | kta | DAYNITE |  | YES | GRDSTOHSTNOC02XTRMN0_E | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Energy | GRDSTOHSTNOCO2XTRMN0_IN |  | GRDSTOHSTNOCO2XTRMN0_OUT | 1 | 2030 |  |  |  | 20 | 20 | 25 | [13 empty] | -3.65 | -3.65 | -3.65 |  | 107.1429 | 107.1429 | 107.1429 |  |  |  | 5.3571 | 5.3571 | 5.3571 | 0.5 | 0.4 | 0.4 | 0
PRE | GRDSTOHSTNOCO2XTRMN0_PO | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Power Out | kt | kta | DAYNITE |  | YES | GRDSTOHSTNOCO2XTRMN0_PO | Grid Storage CO2 Storage - Tanks CO2 Blend Transmission New - Power Out | GRDSTOHSTNOCO2XTRMN0_OUT | ELC | CO2 | 1 | 2030 | 0.01 | 0.01 | 0.01 | 20 | 20 | 25 |  |  |  |  | 0.95 | 0.95 | 0.95 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 1 | 1
ELE | GRDSTOLIONONELCMIDN0_PI | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Power In | PJ | GW | DAYNITE |  | YES | GRDSTOLIONONELCMIDN0_PI | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Power In | ELC |  | GRDSTOLIONONELCMIDN0_IN | 31.536 | 2030 |  |  |  | 20 | 25 | 30 |  |  |  |  | 0.98 | 0.985 | 0.985 | [10 empty] | 0.0001 | 0.0001 | 0.0001 | [9 empty] | 0
STS | GRDSTOLIONONELCMIDN0_E | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Energy | PJ | Pja | DAYNITE |  | YES | GRDSTOLIONONELCMIDN0_E | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Energy | GRDSTOLIONONELCMIDN0_IN |  | GRDSTOLIONONELCMIDN0_OUT | 1 | 2030 |  |  |  | 20 | 25 | 30 | 14000 | 30000 | 50000 | [10 empty] | -0.365 | -0.365 | -0.365 |  | 41945.2222 | 27766.5556 | 22154.1667 |  |  |  | 0.5317 | 0.50216 | 0.47262 | 0.2 | 0.2 | 0.2 | 0
ELE | GRDSTOLIONONELCMIDN0_PO | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Power Out | PJ | GW | DAYNITE |  | YES | GRDSTOLIONONELCMIDN0_PO | Grid Storage Lithium-ion Battery Electricity Medium Voltage New 0 - Power Out | GRDSTOLIONONELCMIDN0_OUT |  | ELC | 31.536 | 2030 |  |  |  | 20 | 25 | 30 |  |  |  |  | 0.97 | 0.975 | 0.975 | [10 empty] | 170.144 | 106.34 | 63.804 | 0.57424 | 0.57424 | 0.57424 | [6 empty] | 1 | 1

## 151a Hydrogen Storage - Tanks
Technology |  | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar)
year |  | 2019 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref | Explanation
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | - | -
cat | par
Energy/technical data
| Form of energy stored | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical
| Application | Local | Local | Local | Local | Local | Local | Local | Local | Local | L |  | Systemorlocal(ifelectricityspecifyalsoifpowerintensiveorenergyintensive)
| Energy storage capacity for one unit [MWh] | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 |  | 1
Output capacity for one unit [MW] | bar: ctrl to -
| Input capacity for one unit [MW] | 0.1 | 0.095 | 0.09 | 0.08 | 0.08 | 0.1 | 0.99 | 0.085 | 0.08 | B | [1, 2]
| Round trip efficiency [%] | 88.29% | 88.29% | 88.96% | 89.65% | 90.24% | 88.29% | 88.29% | 89.75% | 90.24% | C | 1
| - Charge efficiency [%] | 88.29% | 88.29% | 88.96% | 89.65% | 90.24% | 88.29% | 88.29% | 89.75% | 90.24% | D
| - Discharge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | E
| Energy losses during storage [%/period] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | F, K
| Auxiliary electricity consumption [% of output] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | J |  | Expressedonlyforheatandgasstorages
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I
| Planned outage [weeks/year] | 3 | 3 | 2 | 1.5 | 1 | 3 | 3 | 1.5 | 0.5 | G | 3
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 30 | 30
| Construction time [years] | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 |  | 3
Regulation ability |  | -: Only for electricity storage
| Primary regulation [%/30 sec] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | H | 3
| Secondary regulation [%/minute] | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | H | 3
Financial data
| Specific investment [MEUR2015/MWh] | 0.060614 | 0.060614 | 0.047757 | 0.028765 | 0.022331 | 0.060614 | 0.060614 | 0.037485 | 0.022331 |  | 1
| Compressor component [MEUR2015/MWh] | 0.031902 | 0.031902 | 0.025443 | 0.013528 | 0.0084811 | 0.031902 | 0.031902 | 0.016962 | 0.0084811 |  | 1
| Type I tanks component [MEUR2015/MWh] | 0.019141 | 0.019141 | 0.016894 | 0.011857 | 0.010177 | 0.019141 | 0.019141 | 0.015266 | 0.010177 |  | 1
| Installation, equipment, manhours [MEUR2015/MWh] | 0.0095706 | 0.0095706 | 0.0084472 | 0.0067171 | 0.0050887 | 0.0095706 | 0.0095706 | 0.007633 | 0.0050887 |  | 1
| Fixed O&M [EUR2015/MW/year] | 638.04 | 638.04 | 531.7 | 531.7 | 425.36 | 638.04 | 638.04 | 478.53 | 319.02 |  | 1
Variable O&M [EUR2015/MWh] | bar: ctrl to Upper
Technology-specific data |  | -: See table in the specific section
| Gravimetric energy density [kWh/kg] | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
| Volumetric energy density @0oC and 1atm pressure [kWh/m3] | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
| Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 |  | 4
Notes:
A. Cannot be defined since there is no conversion of hydrogen back to electricity in the form of a fuel cell in the system
B. The only power input that is considered is the input for the compressor and does not include power needs for the electrolyzer that is making the hydrogen as described in the system definition. Compressor power input decrease of 5% every 10 years
C. Calculated in the "Energy Efficiency" section. Compressor efficency lineraly improved by 20% until 2050.
D. The charge efficiency is practically the roundrtip efficiency itself as there are almost no losses in the discharge process (See note E)
E. Almost no losses during discharge as it is a physical discharge for a pressurized gas from a valve.
F. Permeation characteristics are neglibile for Type I tanks, see also Technology-specific data.
G. System O&M includes maintenance of the compressor and periodic check of the tanks intergrity.
H. System complies with the frequency regulation requirements from Energinet
I. No hydrogen storage systems are known to have time of forced outage.
J. Compressor consumption is not considered auxiliary. Rest of losses that can be translated into energy losses and consequently more electricity consumption are negligible.
K. Losses are below <1%
L. Stationary short-medium term storage after production from an electrolyzer
References:
<none>

## 180 Lithium Ion Battery
Technology |  | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135)
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Application | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive
| Energy storage capacity for one unit [MWh] | 3.2 | 6 | 7 | 8 | 8 | 5 | 9 | 7 | 12 | A | [2,14]
| Output capacity for one unit [MW] | 9.6 | 18 | 21 | 24 | 24 | 16 | 21 | 22 | 28 | A,B | [2,14]
| Input capacity for one unit [MW] | 1.6 | 3 | 3.5 | 4 | 4 | 2.7 | 3.5 | 3.7 | 4.7 | A,B | [2,14]
| Round trip efficiency [%] AC | 91 | 91 | 92 | 92 | 92 | 90 | 92 | 91 | 94 | C | [3,21,22,51]
| Round trip efficiency [%] DC | 95 | 95 | 96 | 96 | 96 | 95 | 96 | 95 | 97 | C | [3,21,22,51]
| - Charge efficiency [%] | 98 | 98 | 98.5 | 98.5 | 98.5 | 98 | 98.5 | 98 | 99 | D | [2]
| - Discharge efficiency [%] | 97 | 97 | 97.5 | 97.5 | 97.5 | 97 | 98 | 97 | 98 | D | [2]
| Energy losses during storage [%/day] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.15 | E | [18,50,52]
| Forced outage [%] | 0.4 | 0.38 | 0.35 | 0.3 | 0.25 | 0.2 | 0.5 | 0.1 | 0.3 | F
| Planned outage [weeks/year] | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.05 | 0.2 | F
| Technical lifetime [years] | 15 | 20 | 25 | 30 | 30 | 15 | 25 | 20 | 45 | G | [3,5,8,14]
| Construction time [years] | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 |  | [38]
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0 | 0.08 | H | [53]
| Response time from full-rated charge to full-rated discharge [sec] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0 | 0.08 | H | [53]
Financial data
| Specific investment [MEUR2015/MWh] | 1.3697 | 1.1081 | 0.66143 | 0.41898 | 0.27117 | 0.93579 | 1.945 | 0.17652 | 1.0368 | I | [44,48]
| - energy component [MEUR/MWh] | 0.32753 | 0.14037 | 0.065931 | 0.04679 | 0.037219 | 0.074438 | 0.20098 | 0.027648 | 0.12229 | J | [44]
| - capacity component [MEUR/MW] PCS | 0.30839 | 0.28712 | 0.17014 | 0.10634 | 0.063804 | 0.25522 | 0.54233 | 0.042536 | 0.26585 | K | [54–56]
| - other project costs [MEUR/MWh] | 0.11697 | 0.10634 | 0.085072 | 0.05317 | 0.042536 | 0.095706 | 0.11697 | 0.021268 | 0.11697 | L | [22,40,54]
| Fixed O&M [kEUR2015/MW/year] | 0.57424 | 0.57424 | 0.57424 | 0.57424 | 0.57424 | 0.47853 | 0.57424 | 0.42536 | 0.57424 | M | [22]
| Variable O&M [EUR2015/MWh] | 2.2331 | 2.1268 | 1.9141 | 1.8078 | 1.7014 | 0.42536 | 5.955 | 0.31902 | 2.6585 | N | [55]
Technology-specific data
| Energy storage expansion cost [MEUR2015/MWh] | 0.4445 | 0.24671 | 0.151 | 0.09996 | 0.079755 | 0.17014 | 0.27542 | 0.048916 | 0.18716 | O | [44,48]
| Output capacity expansion cost [MEUR2015/MW] | 0.30839 | 0.28712 | 0.17014 | 0.10634 | 0.063804 | 0.25522 | 0.54233 | 0.042536 | 0.26585 | P | [54–56]
| Alternative Investment cost [MEUR2015/MW] | 0.41473 | 0.35092 | 0.21268 | 0.12761 | 0.085072 | 0.29775 | 0.61677 | 0.05317 | 0.32965 | Q | [41,44,48,54–56]
| Lifetime in total number of cycles | 6000 | 14000 | 30000 | 40000 | 50000 | 10000 | 16000 | 20000 | 70000 | R | [3–5,14]
| Specific power [W/kg] | 285 | 315 | 417 | 522 | 627 | 300 | 420 | 450 | 900 | S | [2,24]
| Power density [kW/m3] | 354 | 390 | 519 | 648 | 780 | 450 | 600 | 600 | 1200 | S | [2,24]
| Specific energy [Wh/kg] | 95 | 105 | 139 | 174 | 209 | 100 | 140 | 150 | 300 | S | [2,24]
| Energy density [kWh/m3] | 118 | 130 | 173 | 216 | 260 | 150 | 200 | 200 | 400 | S | [2,24]
Notes
A. One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values for 2020-2030 are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. This unit of 3.2MWh/9.6MW (3C) is a typical size grid scale battery. The Specific investment cost under financial data is provided for a 1MWh : 3MW (3C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
B. Power input/output are set to 0.5/3 times the energy capacity as it is the standard grid-connected LIBs designed for power purposes [2,14]. It is noted that the power capacity is strongly dependent on the battery type and chemistry.
C. The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D. The C-rate is 0.5 during charge and up to 6 during discharge for the Samsung SDI batteries [2,14]. The presented conversion efficiencies assume average discharge C-rates in 2020-2020 around 3 and charge C-rates around 0.5.
E. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
F. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
G. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to reach LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [3,5,8,14].
H. The response time is obtained from simulated response time experiments with hardware in the loop [53].
| I. The system specific forecasts includes rack, TMS, BMS, EMS and PCS (Figure 5). The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [44,48]. The specific investment cost is the total cost of a 1MWh : 3MW (3C) battery, which is the typical grid scale battery defined in note A. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
J. The battery pack cost forecast is provided in Figure 8 and the related text [44].
K. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [54–56] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years. The bidirectional inverter given here has more or less the same charge and discharge capacity (MW).
| L. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [22,40,54]. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
M. Fixed O&M is assumed to be constant, although the O&M may depend on the application [22].
| N. Variable O&M is assumed to be 2.1 EUR/MWh in 2020 with a range of 0.4 – 5.6 [55]. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
O. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [44,48].
P. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [54–56].
| Q. The alternative investment cost in MEUR2020/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [41]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [41,44,48,54–56]. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
R. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
S. Specific power, power density, Specific energy and energy density is provided for discharge mode, starting with the values provided in the section “Typical characteristics and capacities”. A charge/discharge conversion factor of 12 can be derived from this section. For this datasheet, a discharge rate of 3C is assumed. The expected development depends on the successive R&D progress as indicated in the section “Research and development perspectives” [2,24].
References
| [1] | ctrl: Leclanche. Lithium Ion Technology and Product Description, (2018). http://www.leclanche.com/technology-products/leclanche-technology/lithium-ion-cells/
| [2] | ctrl: Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
| [3] | ctrl: L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
| [4] | ctrl: L. Kokam Co. Kokam Li-ion/Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
| [5] | ctrl: StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
| [6] | ctrl: Fronius. Fronius Energy Package, (2018). http://www.fronius.com/en/photovoltaics/products/all-products/solutions/fronius-storage-solution/fronius-energy-package/fronius-energy-package
| [7] | ctrl: Fenecon. Fenecon Commercial 50-series Battery Module ¦ Battery Rack, (2018). https://www.fenecon.de/en_US/page/infocenter#fenecon-industrial
| [8] | ctrl: Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
| [9] | ctrl: S. Weintraub, Electrek. Tesla Gigafactory tour roundup and tidbits: ‘This is the coolest factory in the world’, (2016). https://electrek.co/2016/07/28/tesla-gigafactory-tour-roundup-and-tidbits-this-is-the-coolest-factory-ever/
| [10] | ctrl: M. Kane, InsideEVs. BMW i3 Samsung SDI 94 Ah Battery Rated For 524,000 Miles, (2018). https://insideevs.com/lets-look-at-the-specs-of-the-samsung-sdi-94-ah-battery/
| [11] | ctrl: Qnovo. Inside the Battery of a Nissan Leaf, (2018). https://qnovo.com/inside-the-battery-of-a-nissan-leaf/
| [12] | ctrl: J.M. Tarascon, M. Armand. Issues and challenges facing rechargeable lithium batteries, Nature, 414 (2001) 359. doi:10.1038/35104644
| [13] | ctrl: Shutterstock. Tesla 2170 battery cell stock photos, (2018). https://www.shutterstock.com/search/tesla+2170+battery+cell
| [14] | ctrl: Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
| [15] | ctrl: Inside EVs. LCChem Prismatic Cell, (2018). https://insideevs.com/wp-content/uploads/2015/12/ess_cell1.jpg
| [16] | ctrl: H.C. Hesse, M. Schimpe, D. Kucevic, A. Jossen. Lithium-ion battery storage for the grid - A review of stationary battery storage system design tailored for applications in modern power grids, Energies, 10 (2017) 2107. doi:10.3390/en10122107
| [17] | ctrl: M. Schimpe, M. Naumann, N. Truong, H.C. Hesse, S. Santhanagopalan, A. Saxon, A. Jossen. Energy efficiency evaluation of a stationary lithium-ion battery container storage system via electro-thermal modeling and detailed component analysis, Appl. Energy. 210 (2018) 211. doi:10.1016/j.apenenergy.2017.10.129
| [18] | ctrl: Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
| [19] | ctrl: L. Kokam Co. Lithium Ion Polymer Cells - High Energy High PowerㅣKokam Battery Cells, (2018). http://kokam.com/cell/
| [20] | ctrl: Sempra Renewables. Auwahi Wind, (2012). http://www.semprarenewables.com/project/auwahi-wind/
| [21] | ctrl: A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
| [22] | ctrl: Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
| [23] | ctrl: R. Hidalgo-León et al. A survey of battery energy storage system (BESS), applications and environmental impacts in power systems, 2017 IEEE 2nd ETCM pp. 1–6. doi:10.1109/etcm.2017.8247485.
| [24] | ctrl: LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
| [25] | ctrl: Researchinterfaces. Lithium-ion batteries for large-scale grid energy storage, (2018). https://researchinterfaces.com/lithium-ion-batteries-grid-energy-storage/
| [26] | ctrl: U.S. EPA. Application of Life-Cycle Assessment to Nanoscale Technology: Lithium-ion Batteries for Electric Vehicles, United States Environ. Prot. Agency. (2013) 1–119. doi:10.1038/nchem.2085.
| [27] | ctrl: J.F. Peters, M. Baumann, B. Zimmermann, J. Braun, M. Weil. The environmental impact of Li-Ion batteries and the role of key parameters – A review, Renew. Sustain. Energy Rev. 67 (2017) 491–506. doi:10.1016/j.rser.2016.08.039
| [28] | ctrl: The Washington Post. The environmental impact of cobalt mining, (2018). https://www.washingtonpost.com/news/in-sight/wp/2018/02/28/the-cost-of-cobalt/?utm_term=.eebc6c00f0de
| [29] | ctrl: Visualcapitalist. Nickel: The Secret Driver of the Battery Revolution, (2017). http://www.visualcapitalist.com/nickel-secret-driver-battery-revolution/
| [30] | ctrl: Bloomberg. We’re Going to Need More Lithium, (2017). https://www.bloomberg.com/graphics/2017-lithium-battery-future/
| [31] | ctrl: R. Petibon, J. Xia, L. Ma, M.K.G. Bauer, K.J. Nelson, J.R. Dahn. Electrolyte System for High Voltage Li-Ion Cells, J. Electrochem. Soc. 163 (2016) A2571–A2578. doi:10.1149/2.0321613jes
| [32] | ctrl: A. Casimir, H. Zhang, O. Ogoke, J.C. Amine, J. Lu, G. Wu. Silicon-based anodes for lithium-ion batteries: Effectiveness of materials synthesis and electrode preparation, Nano Energy. 27 (2016) 359–376. doi:10.1016/j.nanoen.2016.07.023
| [33] | ctrl: M. Saulnier, A. Auclair, G. Liang, S.B. Schougaard. Manganese dissolution in lithium-ion positive electrode materials, Solid State Ionics. 294 (2016) 1–5. doi:10.1016/j.ssi.2016.06.007
| [34] | ctrl: E.-Y. Kim, B.-R. Lee, G. Yun, E.-S. Oh, H. Lee. Effects of binder content on manganese dissolution and electrochemical performances of spinel lithium manganese oxide cathodes for lithium ion batteries, Curr. Appl. Phys. 15 (2015) 429–434. doi:10.1016/j.cap.2015.01.029
| [35] | ctrl: S. Lee, E.-Y. Kim, H. Lee, E.-S. Oh. Effects of polymeric binders on electrochemical performances of spinel lithium manganese oxide cathodes in lithium ion batteries, J. Power Sources. 269 (2014) 418–423. doi:10.1016/j.jpowsour.2014.06.167
| [36] | ctrl: eeNews Power Management. Revolutionary solid state rechargeable aluminium-sulfur battery project starts, (2017). http://www.eenewspower.com/news/revolutionary-solid-state-rechargeable-aluminium-sulfur-battery-project-starts
| [37] | ctrl: Ørsted. Ørsted takes first steps into commercial energy storage, (2018). https://orsted.com/en/Media/Newsroom/News/2018/04/Orsted-takes-first-steps-into-commercial-battery-storage
| [38] | ctrl: Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
| [39] | ctrl: Electrek. Tesla quietly brings online its massive - biggest in the world - 80 MWh Powerpack station with Southern California Edison, (2017). https://electrek.co/2017/01/23/tesla-mira-loma-powerpack-station-southern-california-edison/
| [40] | ctrl: Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
| [41] | ctrl: Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
| [42] | ctrl: ABB. Battery energy storage system PQpluS, (2018). https://new.abb.com/high-voltage/capacitors/lv/bess-products/PQpluS
| [43] | ctrl: S. Saylors, Philip C. Kjær. Rasmus Lærke. Ancillary Services Provided from Wind Power Plant Augmented with Energy Storage, (2014). https://www.ieee-pes.org/presentations/gm2014/PESGM2014P-000718.pdf
| [44] | ctrl: Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
| [45] | ctrl: CleanTechnica. $100/kWh Tesla Battery Cells This Year, $100/kWh Tesla Battery Packs In 2020¦, (2018). https://cleantechnica.com/2018/06/09/100-kwh-tesla-battery-cells-this-year-100-kwh-tesla-battery-packs-in-2020/
| [46] | ctrl: Wardsauto. Two Tidbits From CES: Better Cybersecurity and Cheaper EV Batteries, (2017). https://www.wardsauto.com/ideaxchange/two-tidbits-ces
| [47] | ctrl: Visualcapitalist. China Leading the Charge for Lithium-Ion Megafactories, (2017) http://www.visualcapitalist.com/china-leading-charge-lithium-ion-megafactories/
| [48] | ctrl: International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
| [49] | ctrl: Windpower Engineering & Development. Global battery energy-storage system installed capacity will exceed 14 GW by 2020, (2016). https://www.windpowerengineering.com/business-news-projects/global-battery-energy-storage-system-installed-capacity-will-exceed-14-gw-2020/
| [50] | ctrl: International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
| [51] | ctrl: Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
| [52] | ctrl: H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
| [53] | ctrl: D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
| [54] | ctrl: R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
| [55] | ctrl: B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
| [56] | ctrl: G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf

## Ammonia storage
30 | m3 |  | 12.7 | GJ/m3 |  | GJ | 250000 | eur
[5 empty] | 1e-06 | PJ | 100 | m3
1000 | eur/m3
[7 empty] | 1270 | gj
30000 | eur
[9 empty] | flh | 0.5
|  | 0.086957 | MEUR/PJ |  |  |  | 0.00127 | pj
[7 empty] | 393.7008 | MEUR/PJ

## Metanol storage
15.8 | GJ/m3 |  | GJ | 200000 | eur
|  | 1e-06 | PJ | 100 | m3
|  |  |  | 1580 | gj
|  |  |  | 0.00158 | pj
|  |  |  | 253.1646 | MEUR/PJ

## JETFUEL storage
800 kg/m3 |  | 4.302e-05 | PJ/ton JET | 200000 | eur
0.8 | ton/m3 |  |  | 100 | m3
|  | 3.4416e-05 | pj/m3 | 2000 | eur/m3
|  |  |  | 193.7084 | eur/pja

## co2 storage
Online Calculation of carbon dioxide (peacesoftware.de)
|  | 150000 | eur
12 bar
-15 | degrees | 100 | m3 | 1500 | eur/m3
28 | kg/m3
|  |  |  | 53.5714 | eur/kg | meur/kt
|  |  |  | 107.1429 |  | meur/kta